## Ch20 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
2001.3 Permits. For permits to operate aircraft-refueling vehicles, application of flammable or combustible finishes and hot work, see Section 107.2. | 2001.3 Permits. For permits to operate aircraft-refueling vehicles, application of flammable or combustible finishes and hot work, see Section 107.2. |  |  | no change
2007.1 General. Helistops and heliports shall be maintained in accordance with Sections 2007.2 through 2007.8. Helistops and heliports on buildings shall be constructed in accordance with the International Building Code. | (N)2007.1 General. Helistops and heliports shall be maintained in accordance with the applicable building code. |  |  | 2007.1 General. Helistops and heliports shall be maintained in accordance with Sections 2007.2 through 2007.8. |  | There are no maintenance requirements in the applicable building codes.
2007.4 Exits. Exits and stairways shall be maintained in accordance with Section 412.7 of the International Building Code. | 2007.4 Exits. Exits and stairways shall be maintained in accordance with the applicable building code. |  |  | 2007.4 Exits. Exits and stairways shall be maintained in accordance with chapter 10 and the applicable building code. |  | There are no maintenance requirements in the applicable building codes.
2007.5 A building with a rooftop helistop or heliport shall be provided with a Class I or III standpipe system extended to the roof level on which the helistop or heliport is located. All portions of the helistop and heliport area shall be within 150 feet (45 720 mm) of a 21/2-inch (63.5 mm) outlet on the standpipe system. | (N)2007.5 Standpipe systems. Where provided, standpipe systems shall be maintained in accordance with the applicable code. |  | change provided to maintain? Is this primarily a design regulation? | 2007.5 Standpipe systems. A building with a rooftop helistop or heliport provided with a Class I or III standpipe system shall be maintained in accordance with Chapter 9 and remain in accordance with the applicable building code. |  | Provides a reference to Chapter 9 fire protection system maintenance requirements. There are no maintenance requirements in the applicable building codes.
2007.6 Foam fire-protection capabilities shall be provided for rooftop heliports. Such systems shall be designed, installed and maintained in accordance with the applicable provisions of Sections 903, 904 and 905. | (N)2007.6 Foam protection. Where provided, foam fire-protection systems shall be maintained in accordance with the applicable building code. |  | 2007.6 Foam protection. Foam fire-protection capabilities shall be provided for rooftop heliports. Such systems shall be maintained in accordance with the applicable provisions of Sections 903, 904 and 905. | 2007.6 Foam protection. Where provided or required by the applicable building code, foam fire-protection capabilities shall be maintained for rooftop heliports. Such systems shall be maintained in accordance with the applicable provisions of Chapter 9. |  | Provides a reference to Chapter 9 fire protection system maintenance requirements. There are no maintenance requirements in the applicable building codes.

## Ch21 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
2101.1 Scope. Dry cleaning plants and their operations shall comply with the requirements of this chapter. | 2101.2 Permit required. Permits shall be required as set forth in Section 107.2. |  |  | No change
2103.3 Design. The occupancy classification, design and construction of dry cleaning plants shall comply with the applicable requirements of the International Building Code. | 2103.3 Design. The occupancy classification, design and construction of dry cleaning plants shall be maintained in accordance with the applicable building code. |  |  | No change
2104.2.1 Ventilation. Ventilation shall be provided in accordance with Section 502 of the International Mechanical Code and DOL 29 CFR Part 1910.1000, where applicable. | (N)2104.2.1 Ventilation. Ventilation shall be maintained in accordance with the applicable building code. |  | Existing businesses have the issue of setting up portable/temporary fans to exhaust/cool from elevated temperatures of the press equipment. There needs to be a means to cite inadequate ventilation. | 2104.2.1 Ventilation. Adequate ventilation shall be maintained. Systems provided shall remain in accordance with the applicable building code. |  | The building code does not include maintenance requirements.
2104.2.3 Electrical wiring and equipment. Electrical wiring and equipment in dry cleaning rooms or other locations subject to flammable vapors shall be installed in accordance with NFPA 70. | 2104.2.3 Electrical wiring and equipment. Electrical wiring and equipment in dry cleaning rooms or other locations subject to flammable vapors shall be maintained in accordance with the applicable building code. |  | There needs to be a means to cite the installation of new electrical circuits that are not in compliance with requirements for flammable atmospheres. | 2104.2.3 Electrical wiring and equipment. Electrical wiring and equipment in dry cleaning rooms or other locations subject to flammable vapors shall be maintained in accordance with NFPA 70 and Chapter 6. Where provided, such systems and equipment shall compy with the applicable building code. |  | The building code does not include maintenance requirements.
2105.2.3 Ventilation. A mechanical ventilation system which is designed to exhaust 1 cubic foot of air per minute for each square foot of floor area [0.0058 m3/(s • m2)] shall be installed in dry cleaning rooms and in drying rooms. The ventilation system shall operate automatically when the dry cleaning equipment is in operation and shall have manual controls at an approved location. | (N)2105.2.3 Ventilation. Ventilation shall be maintained in accordance with the applicable building code. |  | The ventilation system shall operate when the dry cleaning equipment is in operation and shall maintain controls at an approved location. | 2105.2.3 Ventilation. Ventilation shall be maintained and operated in accordance with the applicable building code. |  | The building code does not include maintenance requirements.
2105.3 Type IV and V systems. Type IV and V dry cleaning systems shall be provided with an automatically activated exhaust ventilation system to maintain a minimum of 100 feet per minute (0.51 m/s) air velocity through the loading door when the door is opened. Such systems for dry cleaning equipment shall comply with the International Mechanical Code. Exception: Dry cleaning units are not required to be provided with exhaust ventilation where an exhaust hood is installed immediately outside of and above the loading door which operates at an airflow rate as follows: Eq0005.jpg(Equation 21-1) where: Q = flow rate exhausted through the hood, cubic feet per minute (m3/s). ALD = area of the loading door, square feet (m2). | (N)2105.3 Types IV and V systems. Types IV and V dry cleaning systems shall be maintained in accordance with the applicable building code. |  | There needs to be a means to cite a change of system type (from what was originally approved) that in turn can require a change of ventilation system. | No change
2106.3 Class II and III solvents. Scouring, brushing, and spotting and pretreating shall be permitted to be conducted with Class II or III solvents. The maximum quantity of Class II or III solvents permitted at any work station shall be 1 gallon (4 L). In other than Group H-2 occupancy, the aggregate quantities of solvents shall not exceed the maximum allowable quantity per control area for use-open system. | 2106.3 Class II or III solvents. Scouring, brushing, and spotting and pretreating shall be permitted to be conducted with Class II or III solvents. The maximum quantity of Class II or III solvents permitted at any work station shall be 1 gallon (4 L). |  |  | 2106.3 Class II and III solvents. Scouring, brushing, and spotting and pretreating shall be permitted to be conducted with Class II or III solvents. The maximum quantity of Class II or III solvents permitted at any work station shall be 1 gallon (4 L). In other than Group H-2 occupancy, the aggregate quantities of solvents shall not exceed the maximum allowable quantity per control area for use-open system. |  | The reference to MAQ is appropirate and important to keep in this section.
2107.1 General equipment requirements. Dry cleaning systems, including dry cleaning units, washing machines, stills, drying cabinets, tumblers and their appurtenances, including pumps, piping, valves, filters and solvent coolers, shall be installed and maintained in accordance with NFPA 32. The construction of buildings in which such systems are located shall comply with the requirements of this section and the International Building Code. | 2107.1 General equipment requirements. Dry cleaning systems, including dry cleaning units, washing machines, stills, drying cabinets, tumblers and their appurtenances, including pumps, piping, valves, filters and solvent coolers, shall be maintained in accordance with NFPA 32. |  |  | No change
2107.2 Type II systems. Type II dry cleaning and solvent tank storage rooms shall not be located below grade or above the lowest floor level of the building and shall comply with Sections 2107.2.1 through 2107.2.3. Exception: Solvent storage tanks installed underground, in vaults or in special enclosures in accordance with Chapter 57. | (N)2107.2 Type II systems. (Section deleted) |  | 2107.2 Type II systems. Type II dry cleaning and solvent tank storage rooms shall not be operated below grade or above the lowest floor level of the building and shall comply with Sections 2107.2.1 through 2107.2.3. Exception: Solvent storage tanks located underground, in vaults or in special enclosures in accordance with Chapter 57 and installed in accordance with the applicable building code. | 2107.2 Type II systems. Type II dry cleaning and solvent tank storage rooms shall be operated in accordance with Sections 2107.2.1 through 2107.2.3. Exception: Solvent storage tanks installed underground, in vaults or in special enclosures in accordance with Chapter 57. |  | If the subsections remain, the main sections should remain as well. The exception is also an important pointer to Chapter 57.
2107.2.2 Number of means of egress. Type II dry cleaning rooms shall have not less than two means of egress doors located at opposite ends of the room, at least one of which shall lead directly to the outside. | (N)2107.2.2 Number of means of egress. The number and means of egress for Type II dry cleaning rooms shall be maintained in accordance with the applicable building code. |  |  | 2107.2.2 Number of means of egress. The number and means of egress for Type II dry cleaning rooms shall be maintained in accordance with Chapter 10 and the applicable building code. |  | The building code does not include maintenance requirements.
2107.2.3 Spill control and secondary containment. Curbs, drains or other provisions for spill control and secondary containment shall be provided in accordance with Section 5004.2 to collect solvent leakage and fire protection water and direct it to a safe location. | 2107.2.3 Spill control and secondary containment. Curbs, drains or other provisions for spill control and secondary containment shall be maintained in accordance with the applicable building code. |  | There needs to be a means to cite spill control / secondary containment measures for the storage of containers awaiting use. | 2107.2.3 Spill control and secondary containment. Curbs, drains or other provisions for spill control and secondary containment shall be maintained in accordance with Section 5004.2 to collect solvent leakage and fire protection water as approved in accordance with the applicable building code. |  | Not construciton. The building code does not include maintenance requirements.
2107.3 Solvent storage tanks. Solvent storage tanks for Class II, IIIA and IIIB liquids shall conform to the requirements of Chapter 57 and be located underground or outside, above ground. Exception: As provided in NFPA 32 for inside storage or treatment tanks. | 2107.3 Solvent storage tanks. Solvent storage tanks for Classes II, IIIA and IIIB liquids shall be maintained in accordance with the applicable building code. |  | 2107.3 Solvent storage tanks. Solvent storage tanks for Class II, IIIA and IIIB liquids shall be maintained to the requirements of Chapter 57 and be located underground or outside, above ground in accordance with the applicable building code. Exception: As provided in NFPA 32 for inside storage or treatment tanks. | 2107.3 Solvent storage tanks. Solvent storage tanks for Class II, IIIA and IIIB liquids shall be maintained in accordance with Chapter 57 and remain as approved in accordance with the applicable building code. Exception: As provided in NFPA 32 for inside storage or treatment tanks. |  | Not construciton. The building code does not include maintenance requirements. The exception allows for compliance with NFPA 32 where applicable.
2108.1 General. Where required by this section, fire protection systems, devices and equipment shall be installed, inspected, tested and maintained in accordance with Chapter 9. | 2108.1 General. Fire protection systems, devices, and equipment shall be maintained in accordance with the applicable building code. |  | 2108.1 General. Fire protection systems, devices and equipment shall be inspected, tested and maintained in accordance with Chapter 9. | 2108.1 General. Fire protection systems, devices and equipment shall be inspected, tested and maintained in accordance with Chapter 9. |  | Not construciton. The building code does not include maintenance requirements. Restores maintenance reference to Chapter 9.
2108.2 Automatic sprinkler system. An automatic sprinkler system shall be installed in accordance with Section 903.3.1.1 throughout dry cleaning plants containing Type II, Type III-A or Type III-B dry cleaning systems. Exceptions: 1.An automatic sprinkler system shall not be required in Type III-A dry cleaning plants where the aggregate quantity of Class III-A solvent in dry cleaning machines and storage does not exceed 330 gallons (1250 L) and dry cleaning machines are equipped with a feature that will accomplish any one of the following: 1.1.Prevent oxygen concentrations from reaching 8 percent or more by volume. 1.2.Keep the temperature of the solvent at least 30°F (16.7°C) below the flash point. 1.3.Maintain the solvent vapor concentration at a level lower than 25 percent of the lower explosive limit (LEL). 1.4.Utilize equipment approved for use in Class I, Division 2 hazardous locations in accordance with NFPA 70. 1.5.Utilize an integrated dry-chemical, clean agent or water-mist automatic fire-extinguishing system designed in accordance with Chapter 9. 2.An automatic sprinkler system shall not be required in Type III-B dry cleaning plants where the aggregate quantity of Class III-B solvent in dry cleaning machines and storage does not exceed 3,300 gallons (12 490 L). | (N)2108.2 Automatic sprinkler system. Where installed, an automatic sprinkler system shall be maintained in accordance with the applicable building code. |  | The needs to be a means to cite failure to maintain any of the measures identified in the Exceptions. | Unless otherwise required by the applicable building code, the following operational conditions are to be maintained in the absence of an automatic sprinkler system: 1.Type III-A dry cleaning plants where the aggregate quantity of Class III-A solvent in dry cleaning machines and storage does not exceed 330 gallons (1250 L) and dry cleaning machines are equipped with a feature that will accomplish any one of the following: 1.1.Prevent oxygen concentrations from reaching 8 percent or more by volume. 1.2.Keep the temperature of the solvent at least 30°F (16.7°C) below the flash point. 1.3.Maintain the solvent vapor concentration at a level lower than 25 percent of the lower explosive limit (LEL). 1.4.Utilize equipment approved for use in Class I, Division 2 hazardous locations in accordance with NFPA 70. 1.5.Utilize an integrated dry-chemical, clean agent or water-mist automatic fire-extinguishing system designed in accordance with Chapter 9. 2. Type III-B dry cleaning plants where the aggregate quantity of Class III-B solvent in dry cleaning machines and storage does not exceed 3,300 gallons (12 490 L). |  | Maintenance of sprinkler systems is covered by 2108.1 and Chapter 9. This section provided specific operational conditions that must be maintained if used in lieu of fire sprinklers.
2108.3 Automatic fire-extinguishing systems. Type II dry cleaning units, washer-extractors, and drying tumblers in Type II dry cleaning plants shall be provided with an approved automatic fire-extinguishing system installed and maintained in accordance with Chapter 9. Exception: Where approved, a manual steam jet not less than 3/4 inch (19 mm) with a continuously available steam supply at a pressure not less than 15 pounds per square inch gauge (psig) (103 kPa) is allowed to be substituted for the automatic fire-extinguishing system. | (N)2108.3 Automatic fire-extinguishing systems. (Section deleted) |  |  | no change

## Ch22 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
2201.2 Permits. Permits shall be required for combustible dust-producing operations as set forth in Section 107.2. | 2201.2 Permits. Permits shall be required for combustible dust-producing operations as set forth in Section 107.2. |  |  | no change

## Ch23 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
2301.1 Scope. Automotive motor fuel-dispensing facilities, marine motor fuel-dispensing facilities, fleet vehicle motor fuel-dispensing facilities, aircraft motor-vehicle fuel-dispensing facilities and repair garages shall be in accordance with this chapter and the International Building Code, International Fuel Gas Code and International Mechanical Code. Such operations shall include both those that are accessible to the public and private operations. | 2301.1 Scope. The operation and maintenance of automotive motor fueldispensing facilities, marine motor fueldispensing facilities, fleet vehicle motor fueldispensing facilities, aircraft motorvehicle fuel-dispensing facilities, and repair garages shall be in accordance with this chapter. Such operations shall include both those that are accessible to the public and private operations. |  |  | no change
2301.2 Permits. Permits shall be required as set forth in Section 107.2. | 2301.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
2301.3 Construction documents. Construction documents shall be submitted for review and approval prior to the installation or construction of automotive, marine or fleet vehicle motor fuel-dispensing facilities and repair garages in accordance with Section 105.4. | (N)2301.3 Construction documents. (Section deleted) |  |  | no change
2301.4 Indoor motor fuel-dispensing facilities. Motor fuel-dispensing facilities located inside buildings shall comply with the International Building Code and NFPA 30A. | (N)2301.4 Indoor motor fuel-dispensing facilities. Motor fuel-dispensing facilities located inside buildings shall be maintained in accordance with NFPA 30A and the applicable building code. |  |  | no change
2301.5 Electrical. Electrical wiring and equipment shall be suitable for the locations in which they are installed and shall comply with Section 605, NFPA 30A and NFPA 70. | (N)2301.5 Electrical. Electrical wiring and equipment shall be maintained in accordance with NFPA 30A and the applicable building code. |  |  | 2301.5 Electrical. Electrical wiring and equipment shall be suitable for the locations in which they are installed in accordance with the applicable building code, and shall be maintained in accordance with Section 605, NFPA 30A and NFPA 70. |  | Not construciton. The building code does not include maintenance requirements. Chapter 8 of NFPA 30A addresses electrical equipment at motor fuel-dispensing facilities and is correlated with NFPA 70. Electrical equipment must be approved for the particular hazards anticipated at motor fuel-dispensing facilities and the hazardous nature of flammable and combustible liquids and gases.
2301.6 Heat-producing appliances. Heat-producing appliances shall be suitable for the locations in which they are installed and shall comply with NFPA 30A and the International Fuel Gas Code or the International Mechanical Code. | 2301.6 Heat-producing appliances. Heatproducing appliances shall be suitable for the locations in which they are installed and shall comply with NFPA 30A. |  |  | 2301.6 Heat-producing appliances. Heatproducing appliances shall be suitable for the locations in which they are located and shall comply with NFPA 30A and the applicable building code. |  | Not construciton. The building code does not include maintenance requirements. Heat-producing appliances are ignition sources. Precautions must be taken when using such appliances around flammable and combustible liquids. NFPA 30A, and the applicable building code provide requirements for the safe use of these appliances.
2303.1 Location of dispensing devices. Dispensing devices shall be located as follows: 1.Ten feet (3048 mm) or more from lot lines. 2.Ten feet (3048 mm) or more from buildings having combustible exterior wall surfaces or buildings having noncombustible exterior wall surfaces that are not part of a 1-hour fire-resistance-rated assembly or buildings having combustible overhangs. Exception: Canopies constructed in accordance with the International Building Code providing weather protection for the fuel islands. 3.Such that all portions of the vehicle being fueled will be on the premises of the motor fuel-dispensing facility. 4.Such that the nozzle, when the hose is fully extended, will not reach within 5 feet (1524 mm) of building openings. 5.Twenty feet (6096 mm) or more from fixed sources of ignition. | (N)2303.1 Location of dispensing devices. Dispensing devices shall be maintained in accordance with the applicable building code. |  |  | 2303.1 Location of dispensing operations. The location of dispensing operations shall be maintained in accordance with the following unless otherwise approved in accordance with the applicable building code: 1.Ten feet (3048 mm) or more from lot lines. 2.Ten feet (3048 mm) or more from buildings having combustible exterior wall surfaces or buildings having noncombustible exterior wall surfaces that are not part of a 1-hour fire-resistance-rated assembly or buildings having combustible overhangs. Exception: Canopies constructed in accordance with the applicable building code providing weather protection for the fuel islands. 3.Such that all portions of the vehicle being fueled will be on the premises of the motor fuel-dispensing facility. 4.Such that the nozzle, when the hose is fully extended, will not reach within 5 feet (1524 mm) of building openings. 5.Twenty feet (6096 mm) or more from fixed sources of ignition. |  | These operational items have been consistently in the code for decades and are an important operational control. In order to reduce the likelihood of motor fuels coming into contact with ignition sources or posing a hazard to persons, adjoining property or on-site buildings, this section provides very specific dispensing operation requirements in relation to buildings, lot lines and ignition sources. These are operational controls, not construction requriements.
2303.2 Emergency disconnect switches. An approved, clearly identified and readily accessible emergency disconnect switch shall be provided at an approved location to stop the transfer of fuel to the fuel dispensers in the event of a fuel spill or other emergency. An emergency disconnect switch for exterior fuel dispensers shall be located within 100 feet (30 480 mm) of, but not less than 20 feet (6096 mm) from, the fuel dispensers. For interior fuel-dispensing operations, the emergency disconnect switch shall be installed at an approved location. Such devices shall be distinctly labeled as: EMERGENCY FUEL SHUTOFF. Signs shall be provided in approved locations. | (N)2303.2 Emergency disconnect switches. Emergency disconnect switches shall be maintained in accordance with the applicable building code. |  |  | 2303.2 Emergency disconnect switches. An approved, clearly identified and readily accessible emergency disconnect switch shall be maintained at an approved location in accordance with the applicable building code to stop the transfer of fuel to the fuel dispensers in the event of a fuel spill or other emergency. Such devices shall be distinctly labeled as: EMERGENCY FUEL SHUTOFF. Signs shall be provided in approved locations. |  | This section establishes the maintenance requirements for emergency disconnect switches to shut off the flow of fuel in an emergency. The switch location must be prominently indicated by an approved sign and access to the switch must be free of any obstructions, such as displayed merchandise. This section does not include specific installation or location requirements as those are provided in the applicable building code.
2304.2.2 Emergency controls. Approved emergency controls shall be provided in accordance with Section 2303.2. | (N)2304.2.2 Emergency controls. Approved emergency controls shall be provided in accordance with the applicable building code. |  |  | 2304.2.2 Emergency controls. Approved emergency controls shall be maintained in accordance with Section 2303.2. |  | Restores reference 2303.2 since the building code does not include maintenance requirements.
2304.3.2 Dispensers. Dispensing devices shall comply with Section 2306.7. Dispensing devices operated by the insertion of coins or currency shall not be used unless approved. | (N)2304.3.2 Dispensers. Dispensing devices shall be maintained in accordance with the applicable building code. |  |  | 2304.3.2 Dispensers. Dispensing devices shall be maintained in accordance with Section 2306.7. Dispensing devices operated by the insertion of coins or currency shall not be used unless approved in accordance with the applicable building code. |  | Restores reference to 2306.7 for maintenance of fuel dispensing devices. Provides operational refernece to ensure that coin or currency devices are not added or modified without approval.
2304.3.3 Emergency controls. Approved emergency controls shall be provided in accordance with Section 2303.2. Emergency controls shall be of a type which is only manually resettable. | 2304.3.3 Emergency controls. Approved emergency controls shall be maintained in accordance with the applicable building code. Emergency controls shall be of a type that is only manually resettable. |  |  | 2304.3.3 Emergency controls. Approved emergency controls shall be maintained in accordance with Section 2303.2. Emergency controls shall be of a type that is only manually resettable. |  | There are not maintenance requirements in the building code. This proposal simply restores reference to maintenance requirements of Section 2303.2.
2304.3.5 Emergency procedures. An approved emergency procedures sign, in addition to the signs required by Section 2305.6, shall be posted in a conspicuous location and shall read: IN CASE OF FIRE, SPILL OR RELEASE 1. USE EMERGENCY PUMP SHUTOFF 2. REPORT THE ACCIDENT! FIRE DEPARTMENT TELEPHONE NO.______ FACILITY ADDRESS _____________________ | 2304.3.5 Emergency procedures. An approved emergency procedures sign, in addition to the signs required by Section 2305.6, shall be posted and maintained in a conspicuous location and shall read: IN CASE OF FIRE SPILL OR RELEASE 1. USE EMERGENCY PUMP SHUTOFF 2. REPORT THE ACCIDENT! FIRE DEPARTMENT TELEPHONE NO.________ FACILITY ADDRESS:______________________ |  |  | no change
2305.2.4 Emergency shutoff valves. Automatic emergency shutoff valves required by Section 2306.7.4 shall be checked not less than once per year by manually tripping the hold-open linkage. | 2305.2.4 Emergency shutoff valves. Automatic emergency shutoff valves shall be checked not less than once each year by manually tripping the hold-open linkage. |  |  | no change
2305.2.5 Leak detectors. Leak detection devices required by Section 2306.7.7.1 shall be checked and tested at least annually in accordance with the manufacturer’s specifications to ensure proper installation and operation. | 2305.2.5 Leak detectors. Leak detection devices shall be checked and tested not less than annually in accordance with the manufacturer's specifications to ensure proper installation and operation. |  |  | no change
2305.4 Sources of ignition. Smoking and open flames shall be prohibited within 20 feet (6096 mm) of a fuel-dispensing device. The engines of vehicles being fueled shall be shut off during fueling. Electrical equipment shall be in accordance with NFPA 70. | 2305.4 Sources of ignition. Smoking and open flames shall be prohibited within 20 feet (6096 mm) of a fuel dispensing device. The engines of vehicles being fueled shall be shut off during fueling. Electrical equipment shall be in accordance with NFPA 70. |  |  | no change
2306.1 General. Storage of flammable and combustible liquids shall be in accordance with Chapter 57 and Sections 2306.2 through 2306.6.3. | 2306.1 General. Operation and maintenance of flammable and combustible liquid motor fuel-dispensing facilities shall be in accordance with Chapter 57 and Sections 2306.2 through 2306.6.3 and other applicable provisions of this code. |  |  | no change
2306.2.1.1 Inventory control and leak detection for underground tanks. Accurate inventory records shall be maintained on underground fuel storage tanks for indication of possible leakage from tanks and piping. The records shall be kept at the premises or made available for inspection by the fire official within 24 hours of a written or verbal request and shall include records for each tank. Where there is more than one system consisting of tanks serving separate pumps or dispensers for a product, the inventory record shall be maintained separately for each tank system. Owners and operators of underground fuel storage tanks shall provide release detection for tanks and piping that routinely contain flammable and combustible liquids in accordance with one of the following methods: 1.Monthly inventory control to detect a release of at least 1.0 percent of flow-through plus 130 gallons (492 L). 2.Manual tank gauging for tanks with 2,000-gallon (7570 L) capacity or less when measurements are taken at the beginning and ending of a 36-hour to 58-hour period during which no liquid is added to or removed from the tank. 3.Tank tightness testing capable of detecting a 0.1-gallon (.3785 L) per hour leak rate. 4.Automatic tank gauging that tests for loss of liquid. 5.Vapor monitoring for vapors within the soil of the tank field. 6.Groundwater monitoring when the groundwater is never more than 20 feet (6096 mm) from the ground surface. 7.Interstitial monitoring between the underground tank and a secondary barrier immediately around or beneath the tank. 8.Other approved methods that have been demonstrated to be as effective in detecting a leak as the methods listed above. A consistent or accidental loss of product shall be immediately reported to the fire official. | 2306.2.1.1 Inventory control and leak detection for underground tanks. Accurate inventory records shall be maintained on underground fuel storage tanks for indication of possible leakage from tanks and piping. The records shall be kept at the premises or made available for inspection by the fire official within 24 hours of a written or verbal request and shall include records for each tank. Where there is more than one system consisting of tanks serving separate pumps or dispensers for a product, the inventory record shall be maintained separately for each tank system. Owners and operators of underground fuel storage tanks shall provide release detection for tanks and piping that routinely contain flammable and combustible liquids in accordance with one of the following methods: 1. Monthly inventory control to detect a release of at least 1.0% of flowthrough plus 130 gallons. 2. Manual tank gauging for tanks with 2,000 gallon capacity or less when measurements are taken at the beginning and ending of a 36-hour to 58-hour period during which no liquid is added to or removed from the tank. 3. Tank tightness testing capable of detecting a 0.1 gallon per hour leak rate. 4. Automatic tank gauging that tests for loss of liquid. 5. Vapor monitoring for vapors within the soil of the tank field. 6. Groundwater monitoring when the groundwater is never more than 20 feet from the ground surface. 7. Interstitial monitoring between the underground tank and a secondary barrier immediately around or beneath the tank.8. Other approved methods that have been demonstrated to be as effective in detecting a leak as the methods listed above. A consistent or accidental loss of product shall be immediately reported to the fire official. |  |  | no change
2306.2.2 Above-ground tanks located inside buildings. Above-ground tanks for the storage of Class I, II and IIIA liquid fuels are allowed to be located in buildings. Such tanks shall be located in special enclosures complying with Section 2306.2.6, in a liquid storage room or a liquid storage warehouse complying with Chapter 57, or shall be listed and labeled as protected above-ground tanks in accordance with UL 2085. | (N)2306.2.2 Aboveground tanks located inside buildings. Aboveground tanks for the storage of Classes I, II and IIIA liquid fuels located in buildings shall be maintained in accordance with the applicable building code. |  | 2306.2.2 Above-ground tanks located inside buildings. Above-ground tanks for the storage of Class I, II and IIIA liquid fuels maintained inside of buildings shall be located in accorance with the applicable building code. Unless otherwise approved, the operation of such indoor tanks shall only occur in special enclosures complying with Section 2306.2.6, in a liquid storage room or a liquid storage warehouse complying with Chapter 57 and the appicable building code, or in listed and labeled as protected above-ground tanks in accordance with UL 2085. | 2306.2.2 Above-ground tanks located inside buildings. Above-ground tanks for the storage of Class I, II and IIA liquid fuels are allowed to be located in buildings where permitted by the applicable building code.
2306.2.3 Above-ground tanks located outside, above grade. Above-ground tanks shall not be used for the storage of Class I, II or III liquid motor fuels, except as provided by this section. 1.Above-ground tanks used for outside, above-grade storage of Class I liquids shall be listed and labeled as protected above-ground tanks in accordance with UL 2085 and shall be in accordance with Chapter 57. Such tanks shall be located in accordance with Table 2306.2.3. 2.Above-ground tanks used for outside, above-grade storage of Class II or IIIA liquids shall be listed and labeled as protected above-ground tanks in accordance with UL 2085 and shall be installed in accordance with Chapter 57. Tank locations shall be in accordance with Table 2306.2.3. Exception: Other above-ground tanks that comply with Chapter 57 where approved by the fire code official. 3.Tanks containing fuels shall not exceed 12,000 gallons (45 420 L) in individual capacity or 48,000 gallons (181 680 L) in aggregate capacity. Installations with the maximum allowable aggregate capacity shall be separated from other such installations by not less than 100 feet (30 480 mm). 4.Tanks located at farms, construction projects, or rural areas shall comply with Section 5706.2. 5.Above-ground tanks used for outside above-grade storage of Class IIIB liquid motor fuel shall be listed and labeled in accordance with UL 142 or listed and labeled as protected above-ground tanks in accordance with UL 2085 and shall be installed in accordance with Chapter 57. Tank locations shall be in accordance with Table 2306.2.3. | (N)2306.2.3 Aboveground tanks located outside above grade. Aboveground tanks located outside shall be maintained in accordance with the applicable building code. |  |  | 2306.2.3 Above-ground tanks located outside above grade. Above-ground tanks shall not be used for the storage of Class I, II or III liquid motor fuels unless approved in accordance with the applicable building code. Tanks located at farms, construction projects or rural areas shall comply with Section 5706.2. |  | The installation and arrangement of tanks is regulated by the applicable building code. The improper use of unapproved tanks is an operational issue. Also includes important reference to Chapter 57 for tank operations at farms and construction sites.
TABLE 2306.2.3 MINIMUM SEPARATION REQUIREMENTS FOR ABOVE-GROUND TANKS | (N) TABLE 2306.2.3 MINIMUM SEPARATION REQUIREMENTS FOR ABOVEGROUND TANKS (Table deleted) |  |  | no change
2306.2.4 Above-ground tanks located in above-grade vaults or below-grade vaults. Above-ground tanks used for storage of Class I, II or IIIA liquid motor fuels are allowed to be installed in vaults located above grade or below grade in accordance with Section 5704.2.8 and shall comply with Sections 2306.2.4.1 and 2306.2.4.2. Tanks in above-grade vaults shall also comply with Table 2306.2.3. | (N)2306.2.4 Aboveground tanks located in above-grade vaults or below-grade vaults. Aboveground tanks located in above-grade vaults or below-grade vaults shall be maintained in accordance with the applicable building code. |  |  | 2306.2.4 Above-ground tanks located in above-grade vaults or below grade vaults. Above-ground tanks used for storage of Class I, II or IIIA liquid motor fuels are allowed to be installed in vaults located above grade or below grade where permitted by the applicable building code. |  | There are no maintenance requirements in the building code. This section provides a reminder to the user that additional requirements may be required by the applicable building code.
2306.2.4.1 Tank capacity limits.Tanks storing Class I and Class II liquids at an individual site shall be limited to a maximum individual capacity of 15,000 gallons (56 775 L) and an aggregate capacity of 48,000 gallons (181 680 L). | (N)2306.2.4.1 Tank capacity limits. (Section deleted) |  |  | 2306.2.4.1 Tank capacity limits. The individual and aggregate capacity of tanks storing Class I and Class II liquids at an individual site shall be limited to the quantities allowed in the applicable building code. NOTE: NEED TO DO A LITERATURE REVIEW OF PREVIOUS CODES TO SEE IF VALUES OTHER THAN 15,000 INDIVIDUAL / 48,000 AGGREGATE WERE EVER ALLOWED. IF NOT, REVERT TO ORIGINAL LANGUAGE. |  |  | 2306.2.4.1 Tank capacity limits.Tanks storing Class I and Class II liquids at an individual site shall remain in accordance with the applicable building and and not exceed the maximum allowable quantities of Chapter 50 unless otherwise approved.
2306.2.4.2 Fleet vehicle motor fuel-dispensing facilities. Tanks storing Class II and Class IIIA liquids at a fleet vehicle motor fuel-dispensing facility shall be limited to a maximum individual capacity of 20,000 gallons (75 700 L) and an aggregate capacity of 80,000 gallons (302 800 L). | (N)2306.2.4.2 Fleet vehicle motor fueldispensing facilities. Tanks storing liquids at a fleet vehicle motor fuel-dispensing facility shall be maintained in accordance with the applicable building code. |  |  | 2306.2.4.2 Fleet vehicle motof fuel-dispensing facilities. The individual capacity and aggregate capacity of tanks storing Class II and Class IIIA liquids at a fleet vehicle motor fuel-dispensing facility shall be limited to the quantities allowed in the applicable building code. NOTE: NEED TO DO LITERATURE REVIEW OF PREVIOUS EDITIONS TO DETERMINE IF QUANTITIES OTHER THAN 20,000 GALLON INDIVIDUAL / 80,000 GALLONS AGGREGATE WERE EVER IN THE CODES. IF NOT, THEN REVERT TO THE ORIGINAL LANGUAGE. |  |  | 2306.2.4.2 Fleet vehicle motof fuel-dispensing facilities. The individual capacity and aggregate capacity of tanks storing Class II and Class IIIA liquids at a fleet vehicle motor fuel-dispensing facility shall be limited to the quantities allowed in the applicable building code and shall not exceed the maximum allowable quantities of Chapter 50 unless otherwise approved.
2306.2.6 Special enclosures. Where installation of tanks in accordance with Section 5704.2.11 is impractical, or because of property or building limitations, tanks for liquid motor fuels are allowed to be installed in buildings in special enclosures in accordance with all of the following: 1.The special enclosure shall be liquid tight and vapor tight. 2.The special enclosure shall not contain backfill. 3.Sides, top and bottom of the special enclosure shall be of reinforced concrete at least 6 inches (152 mm) thick, with openings for inspection through the top only. 4.Tank connections shall be piped or closed such that neither vapors nor liquid can escape into the enclosed space between the special enclosure and any tanks inside the special enclosure. 5.Means shall be provided whereby portable equipment can be employed to discharge to the outside any vapors which might accumulate inside the special enclosure should leakage occur. 6.Tanks containing Class I, II or IIIA liquids inside a special enclosure shall not exceed 6,000 gallons (22 710 L) in individual capacity or 18,000 gallons (68 130 L) in aggregate capacity. 7.Each tank within special enclosures shall be surrounded by a clear space of not less than 3 feet (910 mm) to allow for maintenance and inspection. | (N)2306.2.6 Special enclosures. Special enclosures shall be maintained in accordance with the applicable building code. |  |  | 2306.2.6 Special enclosures. Special enclosures (essentinally concrete vaults) shall be maintained and remain in accordance with the applicable building code. Tanks for liquid motor fuels are allowed to be operated in approved special enclosures where maintained in accordance with the following: 1.The special enclosure shall be maintained liquid tight and vapor tight. 2.The special enclosure shall not contain backfill. 3.Sides, top and bottom of the special enclosure shall be maintained as reinforced concrete, with openings for inspection through the top only. 4.Tank connections shall be maintained as piped or closed such that neither vapors nor liquid can escape into the enclosed space between the special enclosure and any tanks inside the special enclosure. 5.Means shall be maintained whereby portable equipment can be employed to discharge to the outside any vapors which might accumulate inside the special enclosure should leakage occur. 6.Tanks containing Class I, II or IIIA liquids operated inside a special enclosure shall maintain not more than 6,000 gallons (22 710 L) in individual capacity or 18,000 gallons (68 130 L) in aggregate capacity unless otherwise approved by the applicable building code. 7.Unless otherwise approved, each tank within special enclosures shall maintain a clear space of not less than 3 feet (910 mm) to allow for maintenance and inspection. |  | The safe operation within special enclosures is dependent upon maintaining the items listed in this section. There are no maintenance requirements in the building code. Also, language from the commentary as to the concept/definition of special enclosures has been provided for clarity.
2306.5 Secondary containment. Above-ground tanks shall be provided with drainage control or diking in accordance with Chapter 57. Drainage control and diking is not required for listed secondary containment tanks. Secondary containment systems shall be monitored either visually or automatically. Enclosed secondary containment systems shall be provided with emergency venting in accordance with Section 2306.6.2.5. | (N)2306.5 Secondary containment. Aboveground tanks provided with drainage control or diking shall be maintained in accordance with Chapter 57 and the applicable building code. |  |  | 2306.5 Secondary containment. Drainage control or diking for above-ground tanks shall be maintained in accordance with Chapter 57. Secondary containment systems shall be monitored with visually or automatically. Emergency venting for enclosed secondary containment systems shall be maintained and remain in accordance with the applicable building code. NOTE: Drainage control and diking is not required for listed secondary containment tanks. |  | There are no maintenance requirements in the building code. This section restores basic operational requirements such as visual monitoring as well as maintenance of emergency venting if provided. It also add a note, not a requirement, regarding listed secondary containment tanks not requiring drainage or diking.
2306.6 Piping, valves, fittings and ancillary equipment for use with flammable or combustible liquids. The design, fabrication, assembly, testing and inspection of piping, valves, fittings and ancillary equipment for use with flammable or combustible liquids shall be in accordance with Chapter 57 and Sections 2306.6.1 through 2306.6.3. | (N)2306.6 Piping, valves, fittings and ancillary equipment for use with flammable or combustible liquids. The design, fabrication, assembly, testing and inspection of piping, valves, fittings and ancillary equipment for use with flammable or combustible liquids shall be maintained in accordance with the applicable building code |  |  | 2306.6 Piping, valves, fittings and ancillary equipment for use with flammable or combustible liquids. The design, fabrication and assembly of piping, valves, fittings and ancillary equipment shall be in accordance with the applicable building code. The testing and inspection of piping, vlaves, fittings and ancillary equipment for use with flammable or combustible liquids shall be in accordance with Chapter 57 and Sections 2306.6.1 through 2606.6.3. |  | There are no mainteance requirements in the building code. Removes the words "design, fabrication and assmebly" and restores the reference to Chapter 57 for testing/inspection (not construction). The majority of leaks come from piping, valves, fittings and ancillary equipment, not from the tank itself. Therefore, this section is intended to reduce fuel spills by addressing the requirements for this equipment.
2306.6.2 Piping, valves, fittings and ancillary equipment for above-ground tanks for Class I, II and III liquids. Piping, valves, fittings and ancillary equipment for above-ground tanks storing Class I, II and III liquids shall comply with Sections 2306.6.2.1 through 2306.6.2.6. | (N)2306.6.2 Piping, valves, fittings and ancillary equipment for aboveground tanks for Classes I, II and III liquids. Piping, valves, fittings and ancillary equipment for aboveground tanks shall be maintained in accordance with the applicable building code. |  |  | 2306.6.2 Piping, valves, fittings and ancillary equipment for above-ground tanks for Class I, II and III liquids. Piping, valves, fittings and ancillary equipment for above ground tanks storing Class I, II and III liquids shall be maintained in accordance with this section and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code but there are in the following sections.
2306.6.2.1 Tank openings. Tank openings for above-ground tanks shall be through the top only. | (N)2306.6.2.1 Tank openings. (Section deleted) |  |  | 2306.6.2.1 Tank openings. Tank openings for above-ground tanks shall be through the top only unless specifically approved in accordance with the applicable building code. |  | The presence of tank openings or uncovered openings on tanks is an operational concern unless specficially approved during installation.
2306.6.2.2 Fill-pipe connections. The fill pipe for above-ground tanks shall be provided with a means for making a direct connection to the tank vehicle’s fuel-delivery hose so that the delivery of fuel is not exposed to the open air during the filling operation. Where any portion of the fill pipe exterior to the tank extends below the level of the top of the tank, a check valve shall be installed in the fill pipe not more than 12 inches (305 mm) from the fill-hose connection. | (N)2306.6.2.2 Fill-pipe connections. The fill pipe for aboveground tanks shall be maintained in accordance with the applicable building code. |  |  | 2306.6.2.2 Fill-pipe connections. Unless otherwise approved in accordance with the applicable building code, the fill pipe for above-ground tanks shall be provided with a means for making a direct connection to the tank vehicle's fuel-delivery hose so that the delivery of fuel is not exposed to the open air during the filling operation. |  | The exposure of fuel-delivery to the open air is an operational hazard regulated by this section to ensure proper fuel-delievery hose arrangements. This is an opertaional control, not construction.
2306.6.2.3 Overfill protection. Overfill protection shall be provided for above-ground flammable and combustible liquid storage tanks in accordance with Sections 5704.2.7.5.8 and 5704.2.9.7.6. | (N)2306.6.2.3 Overfill protection. Overfill protection shall be in accordance with the applicable building code. |  |  | 2306.6.2.3 Overfill protection. Overfill protection for above-ground flammable and combustible liquid storage tanks shall be maintained in accordance with Chapter 57 and remain in accordance with the applicable building code. |  | Overfill prevention is a major concern when dealing with above-ground tanks. There are no maintenance requirements in the buildling code. This propsal also provides additional context to the maintenance requirements.
2306.6.2.4 Siphon prevention. An approved antisiphon method shall be provided in the piping system to prevent flow of liquid by siphon action. | (N)2306.6.2.4 Siphon prevention. An approved antisiphon method shall be maintained in accordance with the applicable building code. |  |  | 2306.6.2.4 Siphon prevention. Antisiphon methods provided in the piping system to prevent flow of liquid by siphon action shall be maintained and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code. This proposal also provides additional context to the requirements listed. This section requires that an approved anti-siphon device be maintained in the liquid piping near the top of the tank to prevent liquid flow from the tank by siphon action if the supply pipe from the tank to the dispenser is damaged.
2306.6.2.5 Emergency relief venting. Above-ground storage tanks, tank compartments and enclosed secondary containment spaces shall be provided with emergency relief venting in accordance with Chapter 57. | (N)2306.6.2.5 Emergency relief venting. Aboveground storage tanks, tank compartments, and enclosed secondary containment spaces shall be maintained in accordance with the applicable building code. |  |  | 2306.6.2.5 Emergency relief venting. Emergency relief venting for above-ground storage tanks, tank compartments and enclosed secondary containment spaces shall be maintained in accordance with Chapter 57 and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code. This proposal also restores the reference to Chapter 57. The emergency relief vent is the most important safety device installed on the tank. The emergency relief vent prevents the tank from overpressurizing in the event the tank is exposed to fire. In the case of a secondary containment above-ground tank there must be an emergency relief vent maintained for each tank compartment and an emergency relief vent for the interstitial space.
2306.6.2.6 Spill containers. A spill container having a capacity of not less than 5 gallons (19 L) shall be provided for each fill connection. For tanks with a top fill connection, spill containers shall be noncombustible and shall be fixed to the tank and equipped with a manual drain valve that drains into the primary tank. For tanks with a remote fill connection, a portable spill container is allowed. | (N)2306.6.2.6 Spill containers. Spill containers shall be maintained in accordance with the applicable building code. |  |  | 2306.6.2.6 Spill containers. A spill container having a capacity of not less than 5 gallons (19 L) shall be provided for each fill connection. For tanks with a top fill connection, spill containers shall be noncombustible and shall be fixed to the tank and equipped with a manual drain valve that drains into the primary tank unless specifically approved otherwise in accordance with the applicable building code. For tanks wiith a remote fill connection, a portable spill container is allowed. |  | Spill containers are operational items, not construction.
2306.6.3 Piping, valves, fittings and ancillary equipment for underground tanks. Piping, valves, fittings and ancillary equipment for underground tanks shall comply with Chapter 57 and NFPA 30A. | (N)2306.6.3 Piping, valves, fittings and ancillary equipment for underground tanks. Piping, valves, fittings and ancillary equipment for underground tanks shall be maintained in accordance with the applicable building code. |  |  | 2306.6.3 Piping, vlaves, fittings and ancillary equipment for underground tanks. Piping, valves, fittings and ancillary equipment for underground tanks shall be maintained in accordance with Chapter 57 of this code, NFPA 30A and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code. This proposal also restores the reference to Chapter 57 and NFPA 30A.
2306.7 Fuel-dispensing systems for flammable or combustible liquids. The design, fabrication and installation of fuel-dispensing systems for flammable or combustible liquid fuels shall be in accordance with Sections 2306.7.1 through 2306.7.9.2.4. Alcohol-blended fuel-dispensing systems shall also comply with Section 2306.8. | (N)2306.7 Fuel-dispensing systems for flammable or combustible liquids. Fueldispensing systems for flammable or combustible liquid fuels shall be maintained in accordance with the applicable building code. |  |  | 2306.7 Fuel-dispensing systems for flammable and combustible liquids. Fuel dispensing systems for flammable and combustible liquid fuels shall be maintained in accordance with this sections 2306.7.1 through 2306.7.9.2.4 and remain in accordance with the applicable building code. Alcohol-blended fuel-dispensing systems shall also be maintained in accordance with Section 2306.8. |  | There are no maintenance requirements in the building code. This proposal also provides reference to alcohol-blended fuels which is consistent with the original intent of the section. Alternative alcohol-blended fuels, while they are considered in this category of fuels, possess characteristics that require the systems for dispensing them to comply with additional requirements contained in Section 2306.8.
2306.7.1 Listed equipment. Electrical equipment, dispensers, hose, nozzles and submersible or subsurface pumps used in fuel-dispensing systems shall be listed. | (N)2306.7.1 Listed equipment. (Section deleted) |  |  | 2306.7.1 Listed equipment. Electrical equipment, dispensers, hose, nozzles and submersible or subsurface pumps used in fuel dispensing systems shall be listed unless otherwise approved in accordance with the applicable building code. |  | Operational equipment not construction. Ensuring that electrical and dispensing equipment maintain listings is a key operational requirement of the life of a facility. This is consistent with other "Listing" sections of the code. The use of listed equipment and devices provides evidence that they have been evaluated by a thirdparty agency for safe use in the applications for which they are designed. This is especially important where flammable liquids are being transferred or dispensed.
2306.7.2 Fixed pumps required. Class I and II liquids shall be transferred from tanks by means of fixed pumps designed and equipped to allow control of the flow and prevent leakage or accidental discharge. | (N)2306.7.2 Fixed pumps required. (Section deleted) |  |  | 2306.7.2 Fixed pumps required. Unless otherwise approved in accordance with the applicable building code, class I and II liquids shall be transferred from tanks by means of fixed pumps that allow control of the flow and prevent leakage or accidental discharge. |  | Operational requirements not installation of pumps or construction.
2306.7.3 Mounting of dispensers. Dispensing devices, except those installed on top of a protected above-ground tank that qualifies as vehicle-impact resistant, shall be protected against physical damage by mounting on a concrete island 6 inches (152 mm) or more in height, or shall be protected in accordance with Section 312. Dispensing devices shall be installed and securely fastened to their mounting surface in accordance with the dispenser manufacturer’s instructions. Dispensing devices installed indoors shall be located in an approved position where they cannot be struck by an out-of-control vehicle descending a ramp or other slope. | (N)2306.7.3 Mounting of dispensers. Dispensing devices, except those installed on top of a protected aboveground tank that qualifies as vehicle-impact resistant, shall be maintained in accordance with the applicable building code. |  |  | 2306.7.3 Mounting of dispensers. Unless otherwise approved in accordance with the applicable building code, dispensing devices, except those installed on top of a protected above-ground tank that qualifies as vehicle-impact resistant, shall be maintained as protected against physical damage by a concrete island 6 inches (152 mm) or more in height, or shall maintain protection in accordance with Section 312. Dispensing devices shall be maintained securely fastened to their mounting surface in accordance with the dispenser manufacturer's instructions. Dispensing devices installed indoors shall be located in a position where they cannont be struck by an out-of-control vehicle descending a ramp or other slope unless otherwise approved in accordance with the applicable building code. |  | Operational maintenance requirements of dispensing equipment (impact damage protection, securely fastened, etc.) Not construction. These equirements have been consistent in the code since at least the 1978 BOCA edition.
2306.7.4 Dispenser emergency shutoff valve. An approved automatic emergency shutoff valve designed to close in the event of a fire or impact shall be properly installed in the liquid supply line at the base of each dispenser supplied by a remote pump. The valve shall be installed so that the shear groove is flush with or within 1/2 inch (12.7 mm) of the top of the concrete dispenser island and there is clearance provided for maintenance purposes around the valve body and operating parts. The valve shall be installed at the liquid supply line inlet of each overhead-type dispenser. Where installed, a vapor return line located inside the dispenser housing shall have a shear section or approved flexible connector for the liquid supply line emergency shutoff valve to function. Emergency shutoff valves shall be installed and maintained in accordance with the manufacturer’s instructions, tested at the time of initial installation and at least yearly thereafter in accordance with Section 2305.2.4. | (N)2306.7.4 Dispenser emergency shutoff valve. Dispenser emergency shutoff valves shall be maintained in accordance with the applicable building code. |  |  | 2306.7.4 Dispenser emergency shutoff valve. Unless otherwise approved in accordance with the applicable building code, an approved automatic emergency shutoff valve designed to close in the event of a fire or impact shall be maintained in the liquid supply line at the base of dispenser supplied by a remote pump. Such valve shall be maintained and remain in accordance with the applicble building code. Emergency shutoff valves shall be maintained in accordance with the manufacturer's instructions and tested at least yearly in accordance with Section 2305.2.4. |  | Provide context for maintenance of dispenser emergency shutoff valve devices. Restores annual testing requirement that was removed.
2306.7.5 Dispenser hose. Dispenser hoses shall be a maximum of 18 feet (5486 mm) in length unless otherwise approved. Dispenser hoses shall be listed and approved. When not in use, hoses shall be reeled, racked or otherwise protected from damage. | (N)2306.7.5 Dispenser hose. Dispenser hoses shall be maintained in accordance with the applicable building code. |  |  | 2306.7.5 Dispenser hose. Dispenser hoses shall be a maximum of 18 feet (5486 mm) in length unless otherwise approved in accordance with the applicable building code. Dispenser hoses shall be maintained as listed and approved. When not in use, hoses shall be reeled, racked or otherwise protected from damage. |  | Operational equipment requirements for hoses, not construction. Requirements have been consistent and standarized to this limit in the industry and code for years.
2306.7.5.1 Emergency breakaway devices. Dispenser hoses for Class I and II liquids shall be equipped with a listed emergency breakaway device designed to retain liquid on both sides of a breakaway point. Such devices shall be installed and maintained in accordance with the manufacturer’s instructions. Where hoses are attached to hose-retrieving mechanisms, the emergency breakaway device shall be located between the hose nozzle and the point of attachment of the hose-retrieval mechanism to the hose. | (N)2306.7.5.1 Emergency breakaway devices. Emergency breakaway devices shall be maintained in accordance with the applicable building code. |  |  | 2306.7.5.1 Emergency breakaway devices. Unless otherwise approved in accordance with the applicable building code, dispenser hoses for Class I and II liquids shall be maintained with a listed emergency breakaway device designed to retain liquid on both sides of a breakaway point. Such devices shall be maintained in accordance with the manufacturer's instructions. Where hoses are attached to hose retrieving mechanisms, the emergency breakaway device shall remain between the hose nozzle and the point of attachment of the hose-retrieval mechanism to the hose. |  | Important context and specific requirements for the maintenace and operation of emergency breakawy devices. Not construction or installation. This provision requires a breakaway device on dispenser hoses delivering gasoline, diesel and kerosene (Class I and II liquids). These devices are installed to prevent a pull-down of the motor fuel dispenser in the event a car drives away with the hose nozzle valve still in the car’s fill pipe. When these valves operate, the separated sections of the hose are sealed to prevent leakage of liquid from the hose. The placement of the breakaway device between the hose-retrieving mechanism clamp and the nozzle is important to the proper operation of the valve by preventing the pulling force of the driveoff from being transmitted via the retrieving cable directly to the dispenser.
2306.7.6 Fuel delivery nozzles. A listed automatic-closing-type hose nozzle valve with or without a latch-open device shall be provided on island-type dispensers used for dispensing Class I, II or III liquids. Overhead-type dispensing units shall be provided with a listed automatic-closing-type hose nozzle valve without a latch-open device. Exception: A listed automatic-closing-type hose nozzle valve with latch-open device is allowed to be used on overhead-type dispensing units where the design of the system is such that the hose nozzle valve will close automatically in the event the valve is released from a fill opening or upon impact with a driveway. | (N)2306.7.6 Fuel delivery nozzles. Fuel delivery nozzles shall be maintained in accordance with the applicable building code. |  |  | 2306.7.6 Fuel delivery nozzles. Unless specifically approved otherwise in accordance with the applicable building code: island-type dispensers used for dispensing Class I, II or III liquids shall be maintained with a listed automatic-closing-type nozzle valve with or without a latch-open device and overhead-type dispensing units shall be maintained with a listed automatic-closing-type nozzle valve without a latch-open device. Exception: A listed automatic-closing-type hose nozzle valve with latch-open device is allowed to be used on overhead-type dispensing units where the design of the system is such that the hose nozzle valve will close automatically in the event the valve is released from a fill opening or upon impact with a driveway. |  | There are no maintenance requirements in the building code. This proposal restores context to the proper maintenance of fuel delivery nozzles and an optional exception. A listed automatic-closing-type hose nozzle with or without a latch-open device is designed to automatically close when the fuel spits back through the vent line or if the hose nozzle were to fall out of the car fill pipe and strike the ground. When the nozzle is equipped with certain types of vapor recovery equipment, it is designed to shut off when the nozzle is removed from the vehicle. The nozzle on island-type dispensers may or may not be equipped with a latchopen device. The distinction between an overhead-type dispenser and an island-type dispenser is included in this section even though the overhead dispenser is rarely used. However, the concern was that since the hose is on a retractable reel built into the canopy, the nozzle would not strike the ground if it were to fall out of the vehicle and a latch-open device would fail to work, allowing dangerous, uncontrolled fuel spills. The exception is that if the overhead-type dispenser hose mechanism is designed to allow the nozzle to strike the ground and automatically shut off or if the nozzle was equipped with vapor return bellows that would automatically shut off the nozzle if it was removed from the vehicle, the latch-open device would be approved.
2306.7.6.1 Special requirements for nozzles. Where dispensing of Class I, II or III liquids is performed, a listed automatic-closing-type hose nozzle valve shall be used incorporating all of the following features: 1.The hose nozzle valve shall be equipped with an integral latch-open device. 2.When the flow of product is normally controlled by devices or equipment other than the hose nozzle valve, the hose nozzle valve shall not be capable of being opened unless the delivery hose is pressurized. If pressure to the hose is lost, the nozzle shall close automatically. Exception: Vapor recovery nozzles incorporating insertion interlock devices designed to achieve shutoff on disconnect from the vehicle fill pipe. 3.The hose nozzle shall be designed such that the nozzle is retained in the fill pipe during the filling operation. 4.The system shall include listed equipment with a feature that causes or requires the closing of the hose nozzle valve before the product flow can be resumed or before the hose nozzle valve can be replaced in its normal position in the dispenser. | (N)2306.7.6.1 Special requirements for nozzles. (Section deleted) |  |  | No change
2306.7.7 Remote pumping systems. Remote pumping systems for liquid fuels shall comply with Sections 2306.7.7.1 and 2306.7.7.2. | (N)2306.7.7 Remote pumping systems. Remote pumping systems for liquid fuels shall be maintained in accordance with the applicable building code. |  |  | 2306.7.7 Remote pumping systems. Remote pumping systems for liquid fuels shall be maintained in accordance with 2306.7.7.1 and 2306.7.7.2 and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code. Remote pumping systems (sometimes referred to as “pressure systems”) are systems in which liquid motor fuels are transferred from the storage tank to the dispensing devices by submersible pumps located at the storage tank rather than by suction pumps located within the dispensing device. The intent of this section is to maintain special safety devices on pumping systems that deliver fuel to the dispenser by pressure rather than suction.
2306.7.7.1 Leak detection. Where remote pumps are used to supply fuel dispensers, each pump shall have installed on the discharge side a listed leak detection device that will detect a leak in the piping and dispensers and provide an indication. A leak detection device is not required if the piping from the pump discharge to under the dispenser is above ground and visible. | (N)2306.7.7.1 Leak detection. Leak detection devices shall be maintained in accordance with the applicable building code. |  |  | 2306.7.7.1 Leak detection. Leak detection devices shall be maintained. Unless otherwise approved by the applicable building code, where remote pumps are used to supply fuel dispensers, each pump shall maintain a listed leak detection device on the discharge side that will detect a leak in the piping and dispensers and provide an indication of the leak. A leak detection device is not required if the piping from the pump discharge to under the dispenser is above ground and visible. |  | There are no maintenance requirements in the building code. This section highlights operational requirements for leak detection and restores a exception where detection is not necessary. In remote pumping systems, the piping between the remote pump and the dispenser, because it is under pressure, is the number-one location of fuel spills caused by leaks.
2306.7.7.2 Location. Remote pumps installed above grade, outside of buildings, shall be located not less than 10 feet (3048 mm) from lines of adjoining property that can be built upon and not less than 5 feet (1524 mm) from any building opening. Where an outside pump location is impractical, pumps are permitted to be installed inside buildings as provided for dispensers in Section 2301.4 and Chapter 57. Pumps shall be substantially anchored and protected against physical damage. | (N)2306.7.7.2 Location. (Section deleted) |  |  | 2306.7.7.2 Location. Remote pumps installed above grade, outside of buildings, shall remain in approved locations in accordance with the applicable building code. Dispensing operations shall not be less than 10 feet (3048 mm) from lines of adjoining property that can be built upon and not less than 5 feet (1524 mm) from any building opening. Pumps shall be maintained substantially anchored and protected against physical damage. |  | The location of phsyical pumps is to remain as originally approved however it is still importanat to also maintain operational controls which have been consistently in the code for decades. These are not construction requriements.
2306.7.9 Vapor-recovery and vapor-processing systems. Vapor-recovery and vapor-processing systems shall be in accordance with Sections 2306.7.9.1 through 2306.7.9.2.4. | (N)2306.7.9 Vapor-recovery and vaporprocessing systems. Vapor-recovery and vapor-processing systems shall be maintained in accordance with the applicable building code. |  |  | 2306.7.9 Vapor-recovery and vapor-processing systems. Vapor-recovery and vapor-processing system shall be maintained in accordance with sections 2306.7.9.1.1 through 2306.7.9.2.4 and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code. Because of clean-air environmental concerns, some jurisdictions prohibit fuel vapors displaced during tanker deliveries or routine fuel-dispensing operations from being discharged into the atmosphere and require vaporrecovery or vapor-processing systems to prevent pollution. This section contains the provisions for returning the vapors to the tank or processing the vapors on site. Note that the code does not require these systems to be installed, but where they are installed, they must comply with these regulations.
2306.7.9.1 Vapor-balance systems. Vapor-balance systems shall comply with Sections 2306.7.9.1.1 through 2306.7.9.1.5. | (N)2306.7.9.1 Vapor-balance systems. Vapor-balance systems shall be maintained in accordance with the applicable building code. |  |  | 2306.7.9.1 Vapor-balance systems. Vapor balance systems shall be maintained in accordance with section 2306.7.9.1.1 through 2306.7.9.1.5 and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code. As fuel enters the fuel tank of the vehicle it displaces fuel vapors. The vapor-balance system simply captures these vapors and returns them to the storage tank.
2306.7.9.1.1 Dispensing devices. Dispensing devices incorporating provisions for vapor recovery shall be listed and labeled. When existing listed or labeled dispensing devices are modified for vapor recovery, such modifications shall be listed by report by a nationally recognized testing laboratory. The listing by report shall contain a description of the component parts used in the modification and recommended method of installation on specific dispensers. Such report shall be made available on request of the fire code official. Means shall be provided to shut down fuel dispensing in the event the vapor return line becomes blocked. | (N)2306.7.9.1.1 Dispensing devices. Dispensing devices shall be maintained in accordance with the applicable building code. |  |  | 2306.7.9.1.1 Dispensing devices. Dispensing devices incorporating provisions for vapor recovery shall be listed and labeled unless otherwise approved in accordance with the applicable building code. Where dispensing devices are modified for vapor recovery, such modifications shall be approved in accordance with the applicable building code and include a listing report by a nationally recognized testing laboratory. Any listing by report shall contain a desciption of the component parts used in the modification and recommended method of installation on the specific dispensers. Where provided, such report shall be approved by the building official and made available on request of the fire official. Means shall be maintained to shut down fuel dispensing in the event the vapor return line becomes blocked. |  | Clarifies that dispensing equipment is to be listed and any modifications approved by the building official. Motor fuel dispensers equipped with vapor-recovery equipment must be listed and labeled by a recognized testing laboratory attesting that they will function properly when maintained in accordance with the terms of their listing. When existing dispensing equipment is retrofitted with vapor-recovery equipment, the equipment being added must be listed to work with the existing equipment. In other words, a person cannot modify an existing dispensing device manufactured by one company with vapor-recovery component parts manufactured by the same or a different company unless a report from a recognized testing laboratory is submitted to the building official verifying that the retrofit components will work properly with the dispensing device. This is called “listed by report” and is a service provided by major testing laboratories to document equipment compatibility. The report from the testing laboratory must also be provided when requested by the fire official during inspections. Means must be maintained to shut down fuel dispensing in the event the vapor-return line becomes blocked. This provision is self-explanatory. To prevent vapors from entering the atmosphere, the dispensing operation must be stopped if the vapor return is blocked.
2306.7.9.1.2 Vapor-return line closeoff. An acceptable method shall be provided to close off the vapor return line from dispensers when the product is not being dispensed. | (N)2306.7.9.1.2 Vapor-return line closeoff. Vapor-return line closeoffs shall be maintained in accordance with the applicable building code. |  |  | 2306.7.9.1.2 Vapor-return line closeoff. An acceptable method in accordance with the applicable building code shall be maintained as to close off the vapor return line from dispensers when the product is not being dispensed. |  | Operational requirements for the vapor-return line are indicated. To prevent vapors from escaping after dispensing has stopped, some type of device must be maintained that will prevent vapors in the tank from escaping out of the return line. This could be accomplished by a one-way check valve.
2306.7.9.1.3 Piping. Piping in vapor-balance systems shall be in accordance with Sections 5703.6, 5704.2.9 and 5704.2.11. Nonmetallic piping shall be installed in accordance with the manufacturer’s installation instructions. Existing and new vent piping shall be in accordance with Sections 5703.6 and 5704.2. Vapor return piping shall be installed in a manner that drains back to the tank, without sags or traps in which liquid can become trapped. If necessary, because of grade, condensate tanks are allowed in vapor return piping. Condensate tanks shall be designed and installed so that they can be drained without opening. | (N)2306.7.9.1.3 Piping. Piping in vaporbalance systems shall be maintained in accordance with the applicable building code. |  |  | 2306.7.9.1.3 Piping. Piping in vapor-balance systems shall be maintained in accordance with Sections 5703.6, 5704.2.9 and 5704.2.11 of this code. Unless otherwise approved in accordance with the applicable building code, vapor return piping shall be maintained in a manner that drains back to the tank, without sags or traps in which the liquid can become trapped. Where provided, condensate tanks shall be maintained so that they can be drained without opening. |  | There are no maintenance requirements in the building code. This also provides language to make sure that piping continues to be operationally functional.
2306.7.9.1.4 Flexible joints and shear joints. Flexible joints shall be installed in accordance with Section 5703.6.9. An approved shear joint shall be rigidly mounted and connected by a union in the vapor return piping at the base of each dispensing device. The shear joint shall be mounted flush with the top of the surface on which the dispenser is mounted. | (N)2306.7.9.1.4 Flexible joints and shear joints. Flexible joints and shear joints shall be maintained in accordance with the applicable building code. |  |  | 2306.7.9.1.4 Flexible joints and shear joints. Flexible joints shall be maintained in accordance with 5703.6.9. Unless otherwise approved in accordance with the applicable building code, shear joints shall remain rigidly mounted and connected by a union in the vapor return piping at the base of each dispensing device and shall remain mounted flush with the top of the surface on which the dispenser is mounted. |  | There are no maintenance requirements in the building code. The shear joint mentioned here serves the same function for the vapor-recovery lines as the dispenser emergency valve does for the pressurized fuel supply piping to the dispenser (see commentary, Section 2306.7.4). This shear valve must be securely mounted so that the shear groove is located flush or within 1/2 inch (12.7 mm) of the surface of the dispenser island or top of the sump. This shear valve is designed to close in case of a dispenser fire or a dispenser knock-down..
2306.7.9.1.5 Testing. Vapor return lines and vent piping shall be tested in accordance with Section 5703.6.3. | (N)2306.7.9.1.5 Testing. (Section deleted) |  |  | 2306.7.9.1.5 Testing. Existing vapor return lines and vent piping shall be tested in accordance with Section 5703.6.3 where the fire code official has reasonable cause to believe that a leak exists. |  | The ability to test for leaks is a key operational requirement and is not a construction requirement.
2306.7.9.2 Vapor-processing systems. Vapor-processing systems shall comply with Sections 2306.7.9.2.1 through 2306.7.9.2.4. | (N)2306.7.9.2 Vapor-processing systems. Vapor-processing systems shall be maintained in accordance with the applicable building code. |  |  | 2306.7.9.2 Vapor-processing systems. Vapor-processing systems shall be maintained in accordance with section 2306.7.9.2.1 through 2306.7.9.2.4 and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code. Where vapor-recovery systems capture the vapors and return them to the tank, vapor-processing systems do not return the vapors to the tank. Instead, they process the vapors either by refrigeration, absorption or burning them off..
2306.7.9.2.1 Equipment. Equipment in vapor-processing systems, including hose nozzle valves, vapor pumps, flame arresters, fire checks or systems for prevention of flame propagation, controls and vapor-processing equipment, shall be individually listed for the intended use in a specified manner. Vapor-processing systems that introduce air into the underground piping or storage tanks shall be provided with equipment for prevention of flame propagation that has been tested and listed as suitable for the intended use. | (N)2306.7.9.2.1 Equipment. Equipment in vapor-processing systems, including hose nozzle valves, vapor pumps, flame arresters, fire checks or systems for prevention of flame propagation, controls, and vapor-processing equipment, shall be maintained in accordance with the applicable building code. |  |  | 2306.7.9.2.1 Equipment. Unless otherwise approved in accordance with the applicable building code, equipment in vapor-processing-systems, including hose nozzle valves, vapor pumps, flame arresters, fire checks or systems for prevention of flame propagation, controls and vapor-processing equipment, shall be individually maintained as listed for the intended use in a specified manner. Vapor processing systems that introduce air into the underground piping or storage tanks shall maintain equipment for prevention of flame or propagation that has been tested and listed as suitable for the intended use. |  | Maintenance of listing requirements for equipment and devices. Unlisted vapor-processing equipment may not be used. Equipment that is used must be done in accordance with its listing. Vapor-processing systems that introduce air into the underground piping or storage tanks must be provided with equipment for prevention of flame propagation that has been tested and listed as suitable for the intended use. When blowers are used to introduce air, equipment, such as listed flame arresters, must be used to prevent vapors in the flammable range from being ignited.
2306.7.9.2.2 Location. Vapor-processing equipment shall be located at or above grade. Sources of ignition shall be located not less than 50 feet (15 240 mm) from fuel-transfer areas and not less than 18 inches (457 mm) above tank fill openings and tops of dispenser islands. Vapor-processing units shall be located not less than 10 feet (3048 mm) from the nearest building or lot line of a property which can be built upon. Exception: Where the required distances to buildings, lot lines or fuel-transfer areas cannot be obtained, means shall be provided to protect equipment against fire exposure. Acceptable means shall include but not be limited to: 1.Approved protective enclosures, which extend at least 18 inches (457 mm) above the equipment, constructed of fire-resistant or noncombustible materials; or 2.Fire protection using an approved water-spray system. | (N)2306.7.9.2.2 Location. (Section deleted) |  |  | 2306.7.9.2.2 Location. Unless otherwise approved in accordance with the applicable building code, vapor-processing equipment shall remain located at or above grade and vapor processing units shall be operated not less than 10 feet (3048 mm) from the nearest building or lot line of a property which can be building upon. Sources of ignition shall be located not less than 50 feet (15 240 mm) from fuel-transfer areas and not less than 18 inches (457 mm) above tank fill openings and tops of dispenser islands. |  | Important dispensing operation requirements are provided. Not construction. This section is intended to protect vapor-processing equipment from fire exposure, not to protect other structures or equipment from a fire involving the vapor-recovery equipment. Clearance to lot lines is intended to provide a measure of exposure protection to the vapor-processing equipment from potential offsite fires. The exception provides several acceptable clearance alternatives, recognizing that the required clearances cannot, in all cases, be achieved.
2306.7.9.2.2.1 Distance from dispensing devices. Vapor-processing equipment shall be located a minimum of 20 feet (6096 mm) from dispensing devices. | (N)2306.7.9.2.2.1 Distance from dispensing devices. (Section deleted) |  |  | 2306.7.9.2.2.1 Distance from dispensing devices. Unless otherwise approved in accordance with the applicable building code, vapor-processing equipment functioning during dispensing operations shall maintain a minimum of 20 feet (6096 mm) from dispensing devices. |  | Dispensing devices and vapor-processing equipment need to be separated during dispensing operations This is consistent with NFPA 70 for classified flammable vapor areas.
2306.7.9.2.2.2 Physical protection. Vapor-processing equipment shall be protected against physical damage by guardrails, curbs, protective enclosures or fencing. Where approved protective enclosures are used, approved means shall be provided to ventilate the volume within the enclosure to prevent pocketing of flammable vapors. | (N)2306.7.9.2.2.2 Physical protection. Physical protection for vapor-processing equipment shall be maintained in accordance with the applicable building code. |  |  | 2306.7.9.2.2.2 Physical protection. Vapor-processing equipment shall remain protected against physical damage by maintaining guardrails, curbs, protective enclosures or fencing required in accordance with the applicable building code. Where approved protecteive encosures are used, approved means shall be maintained to ventilate the volume within the enclosure to prevent pocketing of flammable vapors. |  | There are no maintenance requirements in the building code. Functional and operational intent is provided for context. Vapor-processing equipment must not only be physically protected from vehicles and other physical damage but, if the protection means includes an enclosure, the enclosed area must be adequately ventilated to prevent the accumulation of flammable vapors within where it could become a hazard to anyone entering the enclosure.
2306.7.9.2.2.3 Downslopes. Where a downslope exists toward the location of the vapor-processing unit from a fuel-transfer area, the fire code official is authorized to require additional separation by distance and height. | (N)2306.7.9.2.2.3 Downslopes. (Section deleted) |  |  | no change
2306.7.9.2.3 Installation. Vapor-processing units shall be securely mounted on concrete, masonry or structural steel supports on concrete or other noncombustible foundations. Vapor-recovery and vapor-processing equipment is allowed to be installed on roofs when approved. | (N)2306.7.9.2.3 Installation. (Section deleted) |  | delete? | 2306.7.9.2.3 Mounting. Unless otherwise approved in accordance with the applicable building code, vapor-processing units shall be maintained securely mounted on concrete, masonry or structural steel supports on concrete or other noncombustible foundations. Vapor-recover and vapor-processing equipment is allowed to be operated on roofs where approved in accordance with the applicable building code. |  | Not construction. Maintenance language for secure mounting as well as a note about roof operations.
2306.7.9.2.4 Piping. Piping in a mechanical-assist system shall be in accordance with Section 5703.6 | (N)2306.7.9.2.4 Piping. Piping in a mechanical-assist system shall be maintained in accordance with the applicable building code. |  |  | 2306.7.9.2.4 Piping. Piping in a mechanical assist system shall be maintained in accordance with 5703.6 and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code.
2306.8 Alcohol-blended fuel-dispensing operations. The design, fabrication and installation of alcohol-blended fuel-dispensing systems shall also be in accordance with Section 2306.7 and Sections 2306.8.1 through 2306.8.5. | (N)2306.8 Alcohol-blended fuel-dispensing operations. Alcohol-blended fueldispensing systems shall be maintained in accordance with the applicable building code. |  |  | 2306.8 Alcohol-blended fuel dispensing operations. Alcohol-blended fuel-dispensing systems shall be maintained in accordnace with 2306.7, Section 2306.8.1 through 2306.8.5 and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code. This section addresses hazards specifically related to the dispensing of alcohol-blended fuels as compared to gasoline and the more established gasoline-alcohol blends (“gasohol”), which are treated the same as gasoline in the code.
2306.8.6 Compatibility. Dispensers shall only be used with the fuels for which they have been listed, which are marked on the product. Field installed components including hose assemblies, breakaway couplings, swivel connectors, and hose nozzle valves shall be provided in accordance with the listing and the marking on the unit. | (N)2306.8.2 Compatibility. (Section deleted) |  |  | 2306.8.6 Compatibility. Dispensers shall only be used with the fuels for which they have been listed, which are marked on the product. Field installed components including hose assemblies, breakaway couplings, swivel connectors, and hose nozzle valves shall be maintained in accordance with the listing and marking on the unit. |  | Compatibility is an ongoing operational issue, not construction. Dispensers and certain field-installed dispensing system components may be made of materials commonly used with gasoline but which may be incompatible with high-level alcohol blends and may degrade over time in their presence. Zinc, brass, lead and aluminum are some of the more sensitive metals. This section requires that dispensers and their field-installed components be marked by the equipment manufacturer with the names of the fuels with which they are compatible, confirming their suitability for use with alcoholblended fuels.
2306.8.3 Facility identification. Facilities dispensing alcohol-blended fuels shall be identified by an approved means. | (N)2306.8.3 Facility identification. (Section deleted) |  |  | 2306.8.3 Facility identification. Facilities dispensing alcohol-blended fuels shall be identified by an approved means. |  | Facility identification is a key firefighter operation and safety issue. Signage is not construction. This section addresses dispensing facility identification for alcohol-blended fuels. Identification of the facility is intended to promote first-responder awareness of the presence of alcohol-blended fuels. According to the U.S. Department of Energy (DOE) Handbook for Handling, Storing, and Dispensing E85, each state, along with the U.S. Department of Transportation (DOT), has developed signage to place at refueling stations. Code users should contact their individual state DOT to obtain the correct signage criteria for their area.
2306.8.4 Marking. Dispensers shall be marked in an approved manner to identify the types of alcohol-blended fuels to be dispensed. | (N)2306.8.4 Marking. (Section deleted) |  |  | 2306.8.4 Marking. Dispensers shall be marked in an approved manner to identify the types of alcohol-blended fuels being dispensed. |  | Dispenser identification is a key firefighter operation and safety issue. Signage is not construction. Identification of equipment for specific alcoholblended fuels communicates the intended use of the installed equipment to both customers and emergency personnel. The Federal Trade Commission (FTC) requires a small sticker to be placed on the face of the fuel dispenser as close as possible to the price per unit of fuel. The sticker should have a black background with orange text
2307.1 General. Motor fuel-dispensing facilities for liquefied petroleum gas (LP-gas) fuel shall be in accordance with this section and Chapter 61. | (N)2307.1 General. Operation and maintenance of motor fuel-dispensing facilities for liquefied petroleum gas (LP-gas) fuel shall be in accordance with this section and other applicable provisions of this code. |  |  | no change
2307.2 Approvals. Storage vessels and equipment used for the storage or dispensing of LP-gas shall be approved or listed in accordance with Sections 2307.2.1 and 2307.2.2. | (N)2307.2 Approvals. (Section deleted) |  |  | 2307.2 Approvals. Unless otherwise approved in accordance with the applicable building code, storage vessels and equipment for the storage or dispensing of LP-gas shall be maintained as approved or listed in accordance with Sections 2307.2.1 and 2307.2.2 and the applicable building code. |  | Using approved storage vessels is an operational issue and is not constuction. All equipment used in connection with the storage and dispensing of LP-gas motor fuel must be either approved or listed, as specified in the following sections.
2307.2.1 Approved equipment. Containers, pressure relief devices (including pressure relief valves), pressure regulators and piping for LP-gas shall be approved. | (N)2307.2.1 Approved equipment. (Section deleted) |  |  | 2307.2.1 Approved equipment. Unless otherwise approved in accordance with the applicable building code, containers, pressure relief devices (including pressure relief valves), pressure regulators and piping for LP-gas shall be approved in accrodance with the applicable building code. |  | Using approved equipment is an operational issue and is not constuction.
2307.2.2 Listed equipment. Hoses, hose connections, vehicle fuel connections, dispensers, LP-gas pumps and electrical equipment used for LP-gas shall be listed. | (N)2307.2.2 Listed equipment. (Section deleted) |  |  | 2307.2.2 Listed equipment. Unless specifically approved otherwise in accordance with the applicable building code, hoses, hose connections, vehicle fuel connections, dispensers, LP-gas pumps and electrical equipment for LP-gas shall be listed in accordance with the applicable building code. |  | Using approved equipment is an operational issue and is not constuction.
2307.3 Attendants. Motor fuel-dispensing operations for LP-gas shall be conducted by qualified attendants or in accordance with Section 2307.6 by persons trained in the proper handling of LP-gas. | 2307.3 Attendants. Motor fuel-dispensing operations for LP-gas shall be conducted by qualified attendants or by persons trained in the proper handling of LP-gas |  |  | 2307.3 Attendants. Motor fuel-dispensing operations for LP-gas shall be conducted by qualified attendants or in accordance with Section 2307.6 by persons trained in the proper handling of LP-gas.. |  | The 2015 VSFPC language give two options that basically mean the same thing to the reader. This proposal restores the reference to trained persons when using privatedly operated and properly maintained dispensers. LP-gas must be dispensed into a vehicle by trained and qualified persons. Unattended and self-service LP-gas stations that are open to the public are not allowed. Section 2307.6 does allow self-service as long as it is closed to the public; that is, the vehicles belong to the operator of the LP-gas-fueling facility and the persons dispensing the fuel are employees of the LP-gas-fueling operation and are properly trained
2307.4 Location of dispensing operations and equipment. In addition to the requirements of Section 2306.7, the point of transfer for LP-gas dispensing operations shall be 25 feet (7620 mm) or more from buildings having combustible exterior wall surfaces, buildings having noncombustible exterior wall surfaces that are not part of a 1-hour fire-resistance-rated assembly, or buildings having combustible overhangs, lot lines of property which could be built on, public streets, or sidewalks and railroads; and at least 10 feet (3048 mm) from driveways and buildings having noncombustible exterior wall surfaces that are part of a fire-resistance-rated assembly having a rating of 1 hour or more. Exception: The point of transfer for LP-gas dispensing operations need not be separated from canopies that are constructed in accordance with the International Building Code and which provide weather protection for the dispensing equipment. LP-gas containers shall be located in accordance with Chapter 61. LP-gas storage and dispensing equipment shall be located outdoors and in accordance with Section 2306.7. | (N)2307.4 Location of dispensing operations and equipment. LP-gas containers shall be located in accordance with the applicable building code. |  |  | 2307.4 Location of dispensing operations and equipment. Unless specifically approved otherwise in accordance with the applicable building code, the point of transfer for LP-gas dispensing operations shall be 25 feet (7620 mm) or more from buildings having combustible exterior wall surfaces, buildings having noncombustible exterior wall surfaces that are not part of a 1-hour fire-resistance-rated assembly, or buildings having combustible overhands, lot lines of propery which could be built on, public streets, or sidewalks and railroads; and at least 10 feet (3048 mm) from driveways and buildings having noncombustible exterior wall surfaces that are part of a fire-resistance-rated assembly having a rating of 1 hour or more. Exception:The point of transfer for LP-gas dispensing operations need not be separated from canopies that are constructed in accodance with the applicable building code and which provide weather protection for the dispensing equipment. LP-gas containers shall remain located in accordance with Chapter 61 and the applicable building code. LP-gas storage and dispensing equipment shall be operated outdoors and in accordance with Section 2306.7 unless othewise approved in accordance with the applicable building code. |  | The location of dispensing operations is a key safety issue that is not a construction requirement. Although technical factors remain in the language, all are options for compliance and are not sole prescriptive construction requirements. This section regulates the location of the point of transfer of the LP gas motor fuel into the vehicle fuel tank. The intent of the term “point of transfer” is to describe the location where LP-gasfueling connections are made and broken and any location where LP-gas is vented during transfer or fueling operations. Whenever LP-gas is dispensed or transferred, there is always at least a “puff” of LP gas released at the point where the LP-gas dispensing hose connects to and disconnects from the vehicle fuel tank or other LP-gas container, and it is at those locations that a flammable mixture will exist, even if momentarily. This section intends to isolate these “movable locations” by regulating how far away from potential ignition sources or other properties they must remain under in all circumstances. This section is also in agreement with NFPA 58 with respect to separation distances
None | (N)2307.5 Additional requirements for LP-gas dispensers and equipment. (Section deleted) |  |  | 2307.5 Additional requirements for LP-gas dispensers and equipment. Unless specifically approved otherwise in accordance with the applicable building code, LP-gas dispensers and related equipment shall remain in accordance with the applicable building code and be maintain the following provisions: 1. Pumps shall remain fixed in place and shall be maintained to allow control of the flow and to prevent leakage and accidental discharge. 2. Dispensing devices operated within 10 feet (3048 mm) of where vehicular traffic occurs shall be protected against physical damage by mounting on a concrete island 6 inches (152 mm) or more in height, or shall be protected in accordance with Section 312. 3. Dispensing devices shall remain securely fastened to their mounting surface in accordance with the dispenser manufacturer's instructions. |  | Additional operational and maintenance language about dispensing. Not construction. In order to reduce the likelihood of a leak or the accidental discharge of LP-gas, Item 1 requires that dispensing pumps be fixed in place and equipped with a means of controlling the flow of LP-gas. Similar to the provisions of Section 2306.7.3, Items 2 and 3 of this section address two alternatives for operating dispensers so as to provide impact protection. One is to mount the dispenser on an elevated island. The other is to protect the dispenser in accordance with Section 312, which requires the dispenser to be protected by steel posts filled with concrete. Regardless of which alternative is chosen, the stability and protection of the dispenser and operation depends on its maintenance in accordance with the manufacturer’s instructions.
2307.5 Installation of LP-gas dispensing devices and equipment. The installation and operation of LP-gas dispensing systems shall be in accordance with Sections 2307.5.1 through 2307.5.3 and Chapter 61. LP-gas dispensers and dispensing stations shall be installed in accordance with the manufacturer’s specifications and their listing. | (N)2307.6 Installation of LP-gas dispensing devices and equipment. (Section deleted) |  |  | 2307.6 Maintenance of LP-gas dispensing devices and equipment. LP-gas dispensing systems shall be maintained and remain in accordance with the applicable building code. The operation of LP-gas dispensing systems shall be in accordance with Sections 2307.5.1 through 2307.5.3 and Chapter 61. LP-gas dispensers and dispensing stations shall be maintained in accordance with the manufacturer's specifications and their listing. |  | Operational requirements and references to other maintenance sections. This provision specifically addresses the maintenance requirements for valves, hoses and impact protection for LPgas-dispensing equipment.
2307.5.1 Valves. A manual shutoff valve and an excess flow-control check valve shall be located in the liquid line between the pump and the dispenser inlet where the dispensing device is installed at a remote location and is not part of a complete storage and dispensing unit mounted on a common base. An excess flow-control check valve or an emergency shutoff valve shall be installed in or on the dispenser at the point at which the dispenser hose is connected to the liquid piping. A differential backpressure valve shall be considered equivalent protection. A listed shutoff valve shall be located at the discharge end of the transfer hose. | (N)2307.6.1 Product control valves. (Section deleted) |  |  | 2307.6.1 Valves. Unless otherwise approved in accordance with the applicable building code, a manual shutoff valve and an excess flow-control check valve shall be maintained in the liquid line between the pump and the dispenser inlet where the dispensing device is installed at a remote location and is not part of a complete storage and dispensing unit moutned on a common base. An excess flow-control check valve or an emergency shutoff valve shall be maintained in or on the dispenser at the point at which the dispenser hose is connected to the liquid piping. A differential backpressure valve shall be considered equivalent protection. A listed shutoff valve shall be maintained at the discharge end of the transfer hose. |  | Maintenance language for valves including options for alternative compliance. The maintenance provisions of this section are similar to certain maintenance provisions in Section 2306.7 that are applicable to flammable and combustible liquid dispensing operations.
2307.5.2 Hoses. Hoses and piping for the dispensing of LP-gas shall be provided with hydrostatic relief valves. The hose length shall not exceed 18 feet (5486 mm). An approved method shall be provided to protect the hose against mechanical damage. | (N)2307.6.2 Hoses. Hoses and piping for the dispensing of LP-gas shall be maintained in accordance with the applicable building code |  |  | 2307.6.2 Hoses. Unless otherwise approved in accordance with the applicable building code, hoses and piping for the dispensing of LP-gas shall maintain hydrostatic relief valves. Hose length for dispensing operations shall not exceed 18 feet (5486 mm). An approved method shall be maintained to protect the hose against mechanical damage. |  | Maintenance of hydrostatic relief valves and other operational requirements. To prevent overpressurization of the hoses and piping, a relief valve must be maintained in the system. The hose length is limited to 18 feet (5486 mm) to prevent excessive amounts of hose from lying on the ground and being damaged by vehicles. The general public is familiar with the 18-foot (5486 mm) length because of the 18-foot (5486 mm) requirement for liquid fuel dispensing hoses in Section 2306.7.5 and they know where to position their vehicles for refueling.
None | (N)2307.6.3 Emergency breakaway devices. (Section deleted) |  |  | 2307.6.3 Emergency breakaway devices. Unless otherwise approved in accordance with the applicable building code, dispenser hoses shall maintain a listed emergency breakaway device to retain liquid on both sides of the breakaway point. Where hoses are attached to hose-retrieving mechanisms, the emergency breakaway device shall be maintained such that the breakaway device activates to protect the dispenser from being dispaced. 2307.6.4 Vehicle impact protection. Where operated within 10 feet of vehicle traffic, LP-gas storage containers, pumps and dispensers shall be protected in accordance with Section 2307.5, Item 2, unless otherwise approved in accordance with the applicable building code. |  | Maintenance of emergency breakaway devices, not installation. Similar to Section 2306.7.5.1 of the code and Section 6.25.4.2 of NFPA 58, this section requires maintenance breakaway devices on dispenser hoses delivering LP-gas motor fuel. These devices prevent a pull-down of the motor fuel dispenser in the event that a car drives away with the hose nozzle valve still attached to the car’s fill pipe. The design of these valves is such that when they operate, the separated sections of the hose are sealed to prevent leakage of fuel from the hose. Where a hose is equipped with a hose retrieval mechanism, placing the breakaway device between the mechanism’s clamp and nozzle is important to the proper operation of the valve by preventing the pulling force of the drive-off from being transmitted via the retrieving cable directly to the dispenser.
|  |  |  | 2307.6.4 Vehicle impact protection. Where operated within 10 feet of vehicle traffic, LP-gas storage containers, pumps and dispensers shall maintain protection in accordance with Section 2307.5, Item 2, unless otherwise approved in accordance with the applicable building code. |  | Maintenance of vehicle impact protection, not installation. This section is intended to prevent leaks and spills caused by vehicle impact by requiring vehicle impact protection.
None | (N)2307.7 Public fueling of motor vehicles. Self-service LP-gas dispensing systems, including key, code, and card lock dispensing systems, shall be limited to the filling of permanently mounted containers providing fuel to the LP-gas powered vehicle. The requirements for self-service LP-gas dispensing systems shall be in accordance with the following: 1. The arrangement and operation of the transfer of product into a vehicle shall be in accordance with this section and Chapter 61. 2. The owner of the LP-gas motor fueldispensing facility or the owner's designee shall provide for the safe operation of the system and the training of users. 3. Portable fire extinguishers shall be provided in accordance with Section 2305.5. 4. Warning signs shall be provided in accordance with Section 2305.6. 5. The area around the dispenser shall be maintained in accordance with Section 2305.7. |  |  | 2307.7 Public fueling of motor vehicles. Self-service LP-gas dispensing systems, including key, code, and card lock dispensing systems, shall be limited to the filling of permanently mounted containers providing fuel to the LP-gas powered vehicle. The requirements for self-service LP-gas dispensing shall be in accordance with the following: 1. The arrangement and operation of the transfer of product into a vehicle shall be in accordance with this section and Chapter 61. 2. Unless otherwise approved in accordance with the applicable building code, the system shall maintain an emergency shut-off switch located in accordance with the applicable building code. 3. The owner of the LP-gas motor fuel-dispensing facility or the owner's designee shall provide for the safe operation of the system and the training of users. 4. Unless otherwise approved in accordance with the applicable building code, the dispenser and hose-end valve shall release not more than 1/8 fluid ounce (4 cc) of liquid to the atmosphere upon breaking the connection with the fill valve on the vehicle. 5. Portable fire extinguishers shall be provided in accordance with Section 2305.5. 6. Warning signs shall be provided in accordance with Section 2305.6. 7. The area around the dispenser shall be maintained in accordance with Section 2306.7. |  | Fueling procedures and equipment function is an operational issue, not construction. This section is in response to new technologies available to safeguard refueling operations. If the vehicles being refueled do not belong to the owner of the fuel dispensing facility and the fuel-dispensing operator is not an employee of the owner, the facility is considered to be “public.” This section allows vehicle owners to refuel their own vehicles under the supervision of, or after having been trained by, the LP-gas motor fuel-dispensing facility owner or the owner’s designee. This section contains provisions for the safe operation of the facility and an emergency shutoff switch similar to the emergency shutoff switch required to be maintained at motor fuel-dispensing facilities in Section 2303.2.
2308.1 General. Motor fuel-dispensing facilities for compressed natural gas (CNG) fuel shall be in accordance with this section and Chapter 53. | 2308.1 General. Motor fuel-dispensing facilities for compressed natural gas (CNG) fuel shall be maintained in accordance with the applicable building code. |  |  | 2308.1 General. Motor fuel-dispensing facilities for compressed natural gas (CNG) fuel shall be maintained and remain in accordance with the applicable building code. Such facilities shall be operated and maintained in accordance with this section and Chapter 53. |  | This proposal restores a key reference to Chapter 53. he federal government is mandating that automakers move toward alternative fuels to replace conventional gasoline and diesel. One of the more popular alternative fuels is compressed natural gas (CNG). As more vehicles use alternative fuels, codes will have to be modified to address the safe dispensing of these fuels. This section addresses the dispensing of CNG at motor fuel-dispensing facilities. Chapter 53 contains the general provisions for CNG.
2308.2.2 Listed equipment. Hoses, hose connections, dispensers, gas detection systems and electrical equipment used for CNG shall be listed. Vehicle-fueling connections shall be listed and labeled. | (N)2308.2.2 Listed equipment. Hoses, hose connections, dispensers, gas detection systems, and electrical equipment used for CNG shall be listed. Vehicle-fueling connections shall be listed and labeled and maintained in accordance with the applicable building code. |  |  | 2308.2 Approvals. Unless otherwise approved in accordance with the applicable building code, storage vessels and equipment used for the storage, compression or dispensing of CNG shall be approved or listed in accordance with Sections 2308.2.1 and 2308.2.2 and the applicable building code. 2308.2.1 Approved equipment. Containers, compressors, pressure relief devices (including pressure relief valves) and pressure regulators and piping used for CNG shall be approved. 2308.2.2 Listed equipment. Hoses, hose connections,dispensers, gas detection systems and electrical equipment used for CNG shall be maintained in accordance with their listing. Vehicle-fueling connections shall be listed and labeled in accordance with the applicable building code.. |  | Maintenance of approvals and listing, not construction. All equipment used in connection with the storage and dispensing of CNG motor fuel must be either approved or listed in accordance with the applicable building code.
2308.3 Location of dispensing operations and equipment. Compression, storage and dispensing equipment shall be located above ground, outside. Exceptions: 1.Compression, storage or dispensing equipment shall be allowed in buildings of noncombustible construction, as set forth in the International Building Code, which are unenclosed for three-quarters or more of the perimeter. 2.Compression, storage and dispensing equipment shall be allowed indoors or in vaults in accordance with Chapter 53. | (N)2308.3 Location of dispensing operations and equipment. (Section deleted) |  |  | 2308.3 Location of dispesning operations and equipment. Unless approved otherwise in accordance with the applicable building code or Chapter 53, compression, storage and dispensing equipment shall be located above ground, outside. |  | Storage, compression and dispensing are functional operations, not construction. Because of the potential for leakage, the compression, storage and dispensing equipment and operations must be located either outdoors or in a noncombustible, substantially open building, except as allowed by Chapter 53.
2308.3.1 Location on property. In addition to the requirements of Section 2303.1, compression, storage and dispensing equipment not located in vaults complying with Chapter 53 shall be installed as follows: 1.Not beneath power lines. 2.Ten feet (3048 mm) or more from the nearest building or lot line that could be built on, public street, sidewalk or source of ignition. Exception: Dispensing equipment need not be separated from canopies that are constructed in accordance with the International Building Code and that provide weather protection for the dispensing equipment. 3.Twenty-five feet (7620 mm) or more from the nearest rail of any railroad track and 50 feet (15 240 mm) or more from the nearest rail of any railroad main track or any railroad or transit line where power for train propulsion is provided by an outside electrical source, such as third rail or overhead catenary. 4.Fifty feet (15 240 mm) or more from the vertical plane below the nearest overhead wire of a trolley bus line. | (N)2308.3.1 Location on property. (Section deleted) |  |  | 2308.3.1 Location of operations on property. Unless otherwise approved in accordance with the applicable building code, compression, storage and dispensing equipment not located in vaults complying with Chapter 53 shall be maintained and operated in accordance with Section 2303.1 and as follows: 1. Not beneath power lines. 2. Ten feet (3048 mm) or more from the nearest building or lot line that could be built on, public street, sidewalk or source of ignition. Exception: Dispensing equipment need not be separated from canopies that are constructed in accordance with the applicable building code and that provide weather protection for the dispensing equipment. 3. Twenty-five feet (7620 mm) or more from the nearest rail of any railroad track and 50 feet (15 240 mm) or more from the nearest rail of any railroad main track or any railroad or transit line where power for train propulsion is provided by an outside electrical source, such as third rail or overhead catenary. 4. Fifty feet (15 240 mm) or more from the vertical plane below the nearest overhead wire of a trolley bus line. |  | Storage, compression and dispensing are functional operations, not construction. Natural gas is lighter than air. The requirements for the operational location of the activity and associated equipment that compresses and dispenses the gas must take this into consideration. The separation distances from overhead ignition sources should be noted.
2308.5 Pressure regulators. Pressure regulators shall be designed and installed or protected so that their operation will not be affected by the elements (freezing rain, sleet, snow or ice), mud or debris. The protection is allowed to be an integral part of the regulator. | (N)2308.5 Pressure regulators. Pressure regulators shall be maintained in accordance with the applicable building code. |  |  | 2308.5 Pressure regulators. Unless otherwise approved in accordance with the applicable building code, pressure regulators shall be maintained so that their operation will not be affected by the elements (freezing rain, sleet, snow or ice), mud or debris. The protection is allowed to be an integral part of the regulator. |  | Maintenance of pressure regulator operations and protection. The pressure regulator must be maintained protected from the elements and is intended to prevent the overpressurization of the vehicle fuel tank and the delivery hose. Pressure regulator failure could result in dangerous overpressure and the opening of relief valves; therefore, they must be dependable. The regulator vent is susceptible to blockage by debris and ice.
2308.6 Valves. Gas piping to equipment shall be provided with a remote, readily accessible manual shutoff valve. | (N)2308.6 Valves. Gas piping to equipment shutoff valves shall be maintained in accordance with the applicable building code. |  |  | 2308.6 Valves. Unless otherwise approved in accordance with the applicable building code, gas piping to equipment shall maintain a remote, readily accessible manual shutoff valve. |  | Maintenace and accessibltiy of a manual shut off valve, not construction. Shutoff valves allow isolation of components for service, repair, replacement and emergency shutdown. This valve is independent of the emergency shutdown device required by Section 2308.7.
2308.7 Emergency shutdown control. An emergency shutdown control shall be located within 75 feet (22 860 mm) of, but not less than 25 feet (7620 mm) from, dispensers and shall also be provided in the compressor area. Upon activation, the emergency shutdown system shall automatically shut off the power supply to the compressor and close valves between the main gas supply and the compressor and between the storage containers and dispensers. | (N)2308.7 Emergency shutdown control. Emergency shutdown controls shall be maintained in accordance with the applicable building code. |  |  | 2308.7 Emergency shutdown control. Emergency shutdown controls shall be maintained and remain within 75 feet (22 860 mm) of, but not less than 25 feet (7620 mm) from, dispensers as well as in the compressor area unless otherwised approved in accordance with the appliable building code. Where provided and, upon activation, the emergency shutdown system shall be maintained to automatically shut off the power supply to the compressor and close valves between the main gas supply and the compressor and between the storage containers and dispensers. |  | Maintenance and operations of emergency shutdown controls. Includes context regarding function of the equipment. CNG systems take natural gas from the utility supply line, compress it to very high pressures and store the compressed gas in vessels from which the dispensers draw the gas for transfer to the vehicle onboard containers. The emergency shutdown device, usually no farther than 75 feet (22 860 mm) from and no closer than 25 feet (7620 mm) to the dispensers, must be maintained. An additional shutdown device must also be maintained near the compressors; the compressors may be remote from the dispensers. The shutdown device must be maintained to disconnect the power to the compressors, must actuate automatic valves that isolate the gas supply from the compressors and isolate the storage vessels from the dispenser, thus limiting accidental gas discharge.
2309.1 General. Hydrogen motor fuel-dispensing and generation facilities shall be in accordance with this section and Chapter 58. Where a fuel-dispensing facility also includes a repair garage, the repair operation shall comply with Section 2311. | 2309.1 General. Operation and maintenance of hydrogen motor fuel-dispensing and generation facilities shall be in accordance with this section and other applicable provisions of this code. Where a fueldispensing facility includes a repair garage, the repair operation shall comply with Section 2311. |  |  | 2309.1 General. Hydrogen motor fuel-dispensing facilities shall be maintained and remain in accordance with the applicable building code. Such facilities shall be operated and maintained in accordance with this section and Chapter 58. Where a fuel-dispensing facility also includes a repair garage, the repair operation shall comply with Section 2311. |  | Restores the important reference to Chapter 58. The federal government is mandating that automakers move toward alternative fuels to replace conventional gasoline and diesel. Hydrogen is one alternative fuel likely to grow in popularity. Section 2309, along with the provisions of Chapter 58, clearly defines gaseous hydrogen refueling and generating stations within the scope of the code and provides fire code officials with the necessary tools to create a safe consumer environment as the use of hydrogen as a motor fuel increases. In many cases, the hydrogen fuel is utilized, with air, within a fuel cell to produce electricity and, in some cases, cogenerate heat. Typically, fire code officials will be faced with two classes of equipment—those that generate hydrogen (for use by other devices) and those that utilize hydrogen as their energy input.
2309.2 Equipment. Equipment used for the generation, compression, storage or dispensing of hydrogen shall be designed for the specific application in accordance with Sections 2309.2.1 through 2309.2.3. | (N)2309.2 Equipment. Equipment used for the generation, compression, storage, or dispensing of hydrogen shall be maintained in accordance with the applicable building code. |  |  | 2309.2 Equipment. Unless otherwise approved in accordance with the applicable building code, equipment used for the generation, compression, storage or dispensing of hydrogen shall be maintained for the specific application in accordance with Sections 2309.2.1 through 2309.2.3. |  | There are no maintenance requirements in the building code. All equipment used in connection with the storage and dispensing of hydrogen motor fuel must be either approved or listed, as specified in the following sections.
2309.2.1 Approved equipment. Cylinders, containers and tanks; pressure relief devices, including pressure valves; hydrogen vaporizers; pressure regulators; and piping used for gaseous hydrogen systems shall be designed and constructed in accordance with Chapters 53, 55 and 58. | (N)2309.2.1 Approved equipment. Cylinders, containers, and tanks; pressure relief devices, including pressure valves; hydrogen vaporizers; pressure regulators; and piping used for gaseous hydrogen systems shall be maintained in accordance with the applicable building code. |  |  | 2309.2.1 Approved equipment. Unless otherwise approved in accordance with the applicable building code, cyclinders, containers and tanks; pressure relief devices, including pressure valves; hydrogen vaporizers; pressure regulators; and piping used for gaseous hydrogen systems shall be maintained in accordance with Chapters 53, 55 and 58. |  | Key maintenance reference to specific chapters. The equipment identified in this section must be approved. Listing of the specified components could be the basis for approval, but listing is not mandated. Any such components must be designed and recommended for the application by the manufacturer.
2309.2.2 Listed or approved equipment. Hoses, hose connections, compressors, hydrogen generators, dispensers, detection systems and electrical equipment used for hydrogen shall be listed or approved for use with hydrogen. Hydrogen motor-fueling connections shall be listed and labeled or approved for use with hydrogen. | (N)2309.2.2 Listed or approved equipment. Hoses, hose connections, compressors, hydrogen generators, dispensers, detection systems, and electrical equipment used for hydrogen shall be listed or approved for use with hydrogen and maintained in accordance with the applicable building code. |  |  | 2309.2.2 Listed or approved equipment. Unless otherwise approved in accordance with the applicable building code, hoses, hose connections, compressors, hydrogen generators, dispensers, detection systems and electrical equipment used for hydrogen shall be maintained as listed or approved for use with hydrogen. Hydrogen motor-fueling connections shall remain listed and labeled or approved for use with hydrogen in accordance with the applicable buildling code. |  | Maintenance of listings and approvals, not construction. The equipment identified in this section must be approved. Listing of the specified components could be the basis for approval, but listing is not mandated. Any such components must be designed and recommended for the application by the manufacturer.
2309.2.3 Electrical equipment. Electrical installations shall be in accordance with NFPA 70. | (N)2309.2.3 Electrical equipment. Electrical installations shall be maintained in accordance with the applicable building code. |  |  | 2309.2.3 Electrical equipment. Electrical installations shall be maintained and remain in accordance with the applicable building code. Portable or temporary electrical equipment shall be in accordance with NFPA 70. |  | There are no maintenance requirements in the building code. This section addresses electrical equipment at hydrogen motor fuel-dispensing facilities and is correlated with NFPA 70. Electrical equipment use must be approved for the particular hazards anticipated at hydrogen motor fuel-dispensing facilities.
2309.3 Location on property. In addition to the requirements of Section 2303.1, dispensing equipment shall be located in accordance with Sections 2309.3.1 through Section 2309.3.2. | (N)2309.3 Location on property. Location of dispensing equipment shall be maintained in accordance with the applicable building code. |  |  | 2309.3 Location on property. Unless otherwise approved in accordance with the applicable building code, dispensing equipment operations shall be remain located in accordance with the applicable buildling code and maintained in accordanc with Section 2301.1 and Sections 2309.3.1 through 2309.3.2. |  | Dispensing area operational requirements, not construction. In order to reduce the likelihood of hydrogen motor fuels coming into contact with ignition sources or posing a hazard to persons, adjoining property or on-site buildings, this section provides dispensing equipment operation location requirements in relation to outdoor equipment, canopies and overhead power lines.
2309.3.1.1 Outdoors. Generation, compression, or storage equipment shall be allowed outdoors in accordance with Chapter 58. | (N)2309.3.1.1 Outdoors. Generation, compression, or storage equipment shall be maintained in accordance with the applicable building code. |  |  | 2309.3.1.1 Outdoors. Generation, compression, or storage equipment shall be allowed outdoors where maintained in accordance with Chapter 58 and NFPA 2. |  | Generation, compression or storage are operational activities, not construction. Restores reference to Chatper 58. This section requires that hydrogen generation, compression and storage equipment installed outdoors be provided with the minimum separations prescribed by Chapter 58 and NFPA 2.
2309.3.1.2 Indoors. Generation, compression, storage and dispensing equipment shall be located in indoor rooms or areas constructed in accordance with the requirements of the International Building Code, the International Fuel Gas Code and the International Mechanical Code and one of the following: 1.Inside a building in a hydrogen cutoff room designed and constructed in accordance with Section 421 of the International Building Code. 2.Inside a building not in a hydrogen cutoff room where the gaseous hydrogen system is listed and labeled for indoor installation and installed in accordance with the manufacturer’s installation instructions. 3.Inside a building in a dedicated hydrogen fuel-dispensing area having an aggregate hydrogen delivery capacity no greater than 12 standard cubic feet per minute (SCFM) and designed and constructed in accordance with Section 703.1 of the International Fuel Gas Code. | (N)2309.3.1.2 Indoors. Generation, compression, storage and dispensing equipment shall be maintained in accordance with the applicable building code. |  |  | 2309.3.1.2 Indoors. Generation, compression, storage and dispensing equipment operations located in indoor rooms or other approved areas shall remain in accordance with the requirements of the applicable building code and NFPA 2 including ventiallation. |  | Location of generation, compression, storage and dispensing operations, not construction. The overriding theme of the indoor location requirements for the generation, compression, storage or dispensing of hydrogen motor fuel is to never permit the maximum concentration of flammable contaminants in air to exceed 25 percent of the lower flammable limit (LFL) for hydrogen during the period that a credible leak exists. This can be accomplished using natural or mechanical means to maintain adequate ventilation to prevent a hazardous buildup of hydrogen gas in buildings or confined spaces.
2309.3.1.3 Gaseous hydrogen storage. Storage of gaseous hydrogen shall be in accordance with Chapters 53 and 58. | (N)2309.3.1.3 Gaseous hydrogen storage. Storage of gaseous hydrogen shall be maintained in accordance with the applicable building code. |  |  | 2309.3.1.3 Gaseous hydrogen storage. Unless otherwise approved in accordance with the applicable building code, storage of gaseous hydrogen shall be in accordance with Chapters 53 and 58. |  | There are no maintenance requirements in the building code. This proposal restores important references to Chapters 53 and 58. Although Section 2309 includes substantial safeguards for the generation, compression, storage or dispensing of hydrogen motor fuel, gaseous hydrogen is also classified as a flammable gas requiring compliance with Chapter 58 and possesses compressed gas hazards requiring compliance with Chapter 53.
2309.3.1.4 Liquefied hydrogen storage. Storage of liquefied hydrogen shall be in accordance with Chapters 55 and 58. | (N)2309.3.1.4 Liquefied hydrogen storage. Storage of liquefied hydrogen shall be maintained in accordance with the applicable building code. |  |  | 2309.3.1.4 Liquified hydrogen storage. Unless otherwise approved in accordance with the applicable building code, storage of liquified hydrogen shall be in accordance with Chapters 55 and 58. |  | Storage is an operational activity, not construction. Although Section 2309 includes substantial safeguards for the generation, compression, storage or dispensing of hydrogen motor fuel, stored liquefied hydrogen is also classified as a flammable cryogenic fluid requiring compliance with Chapter 55, which in turn requires compliance with NFPA 55. Chapter 58 is referenced because it includes requirements for underground liquid hydrogen storage tanks.
2309.3.1.5 Canopy tops. Gaseous hydrogen compression and storage equipment located on top of motor fuel-dispensing facility canopies shall be in accordance with Sections 2309.3.1.5.1 through 2309.3.1.5.5, Chapters 53 and 58 and the International Fuel Gas Code. | (N)2309.3.1.5 Canopy tops. Gaseous hydrogen compression and storage equipment located on top of motor fueldispensing facility canopies shall be maintained in accordance with the applicable building code. |  |  | 2309.3.1.5 Canopy tops. Unless otherwise approved in accordance with the applicable building code, gaseous hydrogen compression and storage equipment operations located on top of motor fuel-dispensing canopies shall be maintained in accordance with Sections 2309.3.1.5.1 through 2309.3.1.5.5, Chapters 53 and 58 and the applicable building code. |  | Regulations for operations on top of canopies, not construction. Overhead placement enhances safety because the equipment remains removed from possible vehicular impact and ground-level ignition sources. This option has gained popularity, especially in more congested urban areas where real estate prices prohibit the purchase of sufficient property to meet the separation requirements of IFC Section 2309.3.2.5.1 for new motor fuel-dispensing facilities.
2309.3.1.5.1 Construction. Canopies shall be constructed in accordance with the motor fuel-dispensing facility canopy requirements of Section 406.7 of the International Building Code. | (N)2309.3.1.5.1 Construction. (Section deleted) |  |  | 2309.3.1.5.1 Construction. Canopy construction shall be maintained and remain in accordance with the applicable building code. NOTE: See Motor Fuel Dispensing Canopy Requirements of the applicable building code. |  | Maintenance of construction, not construction. VCC Section 406.7.2 regulates installation of motor fuel-dispensing facility canopies and includes special requirements for canopies used to support hydrogen motor fuel equipment.
2309.3.1.5.2 Fire-extinguishing systems. Fuel-dispensing areas under canopies shall be equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1. The design of the sprinkler system shall not be less than that required for Extra Hazard Group 2 occupancies. Operation of the sprinkler system shall activate the emergency functions of Sections 2309.3.1.5.3 and 2309.3.1.5.4. | (N)2309.3.1.5.2 Fire-extinguishing systems. Fire-extinguishing provided for fuel-dispensing areas under canopies shall be maintained in accordance with the applicable building code. |  |  | 2309.3.1.5.2 Fire Extinguishing systems. Fire-extinguishing systems provided for fuel-dispensing areas under canopies shall be maintained in accordance with Chapter 9 and remain in accordance with the applicable building code. |  | Removes construction language and provides maintenance language with pointer to Chapter 9
2309.3.1.5.3 Emergency discharge. Operation of the automatic sprinkler system shall activate an automatic emergency discharge system, which will discharge the hydrogen gas from the equipment on the canopy top through the vent pipe system. | (N)2309.3.1.5.3 Emergency discharge. (Section deleted) |  |  | 2309.3.1.5.3 Emergency discharge. Where provided, operation of the fire extinguishing system shall be maintained to activate an automatic emergency discharge system which will discharge the hydrogen gas from the equipment on the canopy top through the vent pipe system. |  | Maintenance of emergency discharge. As part of protecting the hydrogen equipment mounted on top of the canopy from a fire developing below, this section requires that an approved emergency discharge system be provided to “dump” the hydrogen content of the system safely into the atmosphere.
2309.3.1.5.4 Emergency shutdown control. Operation of the automatic sprinkler system shall activate the emergency shutdown control required by Section 2309.5.3. | (N)2309.3.1.5.4 Emergency shutdown control. (Section deleted) |  |  | 2309.3.1.5.4 Emergency shutdown control. Where provided, operation of the fire extinguishing system shall be maintained to activate the emergency shutdown control required to be maintained by Section 2309.5.3. |  | Maintenance of emergency shutdown Whereas Section 2309.3.2.6.2.1 requires maintenance of a precautionary hydrogen “dump” proceedure from the canopy-mounted hydrogen equipment, this section requires maintenance of the emergency shutoff such process where also required to operate upon fire extinguishing system activation.
2309.3.2 Canopies. Dispensing equipment need not be separated from canopies of Type I or II construction that are constructed in a manner that prevents the accumulation of hydrogen gas and in accordance with Section 406.7 of the International Building Code. | (N)2309.3.2 Canopies. (Section deleted) |  |  | no change
2309.4.1 Dispensing systems. Dispensing systems shall be equipped with an overpressure protection device set at 140 percent of the service pressure of the fueling nozzle it supplies. | (N)2309.4.1 Dispensing systems. Dispensing systems shall be maintained in accordance with the applicable building code. |  |  | 2309.4.1 Dispensing systems. Unless otherwise approved in accordance with the applicable building code, dispensing systems with an overpressure protection device shall be maintained set at 140 percent of the service pressure of the fueling nozzle it supplies. |  | Maintenance of overpressue protection device with technical data. This section provides the overpressure protection of the vehicle fuel system by the fuel-dispensing system. Nearly all of the hydrogen fuel cell vehicles that are currently deployed or will be deployed in the near future rely on the fuel dispenser for overpressure protection. Similar language appears in NFPA 52.
2309.5 Safety precautions. Safety precautions at hydrogen motor fuel-dispensing and generation facilities shall be in accordance with Sections 2309.5.1 through 2309.5.3.1. | (N)2309.5 Safety precautions. Safety precautions at hydrogen motor fueldispensing and generation facilities shall be in accordance with Sections 2309.5.1 through 2309.5.3. |  |  | 2309.5.3 Safety precautions. Safety precautions at hydrogen motor fuel-dispensing and generation facilities shall be in accordance with Section 2309.5.1 through 2309.5.3.1. |  | Scoping language. This section establishes a minimum level of safety for hydrogen motor fuel generation and dispensing.
2309.5.2 Emergency shutoff valves. A manual emergency shutoff valve shall be provided to shut down the flow of gas from the hydrogen supply to the piping system. | (N)2309.5.2 Emergency shutoff valves. Manual emergency shutoff valves shall be maintained in accordance with the applicable building code. |  |  | 2309.5.2 Emergency shutoff valves. Unless otherwise approved in accordance with the applicable building code, a manual emergency shutoff valve shall be maintained to shut down the flow of gas from the hydrogen supply to the piping system. |  | Maintenace of shutoff valves. To prevent spillage and to allow servicing of equipment, a remote accessible manual shutoff valve must be maintained. This valve is independent of the emergency shutdown equipment referenced in Section 2309.5.3.
2309.5.3 Emergency shutdown controls. In addition to the manual emergency shutoff valve required by Section 2309.5.2, a remotely located, manually activated emergency shutdown control shall be provided. An emergency shutdown control shall be located within 75 feet (22 860 mm) of, but not less than 25 feet (7620 mm) from, dispensers and hydrogen generators. | (N)2309.5.3 Emergency shutdown controls. Emergency shutdown controls shall be maintained in accordance with the applicable building code. |  |  | 2309.5.3 Emergency shutdown controls. Unless otherwise approved in accordance with the applicable building code, a remotely located, manually activated shutdown control shall be maintained in addition to the manual emergency shutoff valve referenced by Section 2309.5.2. This emergency shutdown control shall be maintained within 75 feet (22 860 mm) of, but not less than 25 feet (7620 mm) from, dispensers and hydrogen generators unless otherwise approved by the applicable building code. |  | Maintenace of shutdown controls, not construction. Two emergency shutdown devices must be maintained, one in the compressor area in accordance with Section 2309.5.2 and the other no closer than 25 feet (7620 mm) or farther than 75 feet (22 860 mm) from the dispenser. These distances and devices are to be maintained at a location such that the emergency shutdown control is, at its furthest, no further from the hydrogen dispensers or generators than a portable fire extinguisher would be but not close enough to put personnel at risk of injury in the event of an emergency.
2309.5.3.1 System requirements. Activation of the emergency shutdown control shall automatically shut off the power supply to all hydrogen storage, compression and dispensing equipment; shut off natural gas or other fuel supply to the hydrogen generator; and close valves between the main supply and the compressor and between the storage containers and dispensing equipment. | (N)2309.5.3.1 System requirements. (Section deleted) |  |  | 2309.5.3.1 System requirements. Unless otherwise approved in accordance with the applicable building code, activation of the emergency shutdown control shall be maintained to automatically shut off the power supply to all hydrogen storage, compression and dispensing equipment; shut off natural gas or other fuel supply to the hydrogen generator; and close valves between the main supply and the compressor and between the storage containers and dispensing equipment. |  | Maintenance of system shutdown operations, not installation. Emergency shutdown controls must be maintained to shut down the power supply to the hydrogen storage, compression and dispensing equipment and close the valves leading to and from the compressor and between the storage containers and dispensers in the event of an emergency. Activation of any one emergency shutdown device must be maintained to activate total shutdown of all generation and dispensing operations on site.
None | (N)2309.6.1.2.1.2 Vent pipe maximum diameter. Vent pipe diameter shall be maintained in accordance with the applicable building code. |  |  | 2309.6.1.2.1.2 Vent pipe maximum diameter. Unless otherwise approved in accordance with the applicable building code, defueling vent pipes shall maintain a maximum inside diameter of 1 inch (25 mm). |  | Maintenance of vent pipe size including a minimum threshold for successful operations. When discharging hydrogen to the atmosphere, it is important that the size of the vent pipe on the equipment be such that it will provide sufficient discharge velocity to disperse the hydrogen in the air.
None | (N)2309.6.1.2.1.3 Maximum flow rate. The maximum rate of hydrogen flow through the vent pipe system shall be maintained in accordance with the applicable building code. |  |  | 2309.6.1.2.1.3 Maximum flow rate. Unless otherwise approved in accordance with the applicable building code, the maximum rate of hydrogen flow through the vent pipe system shall not exceed 1,000 cfm at NTP (0.47 m3/s) and shall be controlled by means of the manufacturer's equipment, at low pressure and without adjustment. |  | When gas flows through piping, friction with the pipe wall generates heat. Limiting the flow rate limits the amount of heat generated by the flow of gas. This is an operational control, not construction.
None | (N)2309.6.1.2.2 Construction documents. (Section deleted) |  |  | 2309.6.1.2.2 System documentation. System documentation illustrating the defueling system to be utilized shall be provided. Documentation shall be of sufficient detail and clarity to allow for evaluation of the piping and control systems to be utilized and include the method of support for cylinders, containers or tanks to be used as part of a closed transfer system, the method of grounding and bonding and other requirements specified herein. |  | Defueling systems and equipment are operational componets of a repair garage. Each system can be differnet and it is important for the fire official to have access to the system documents to ensure that they are being used and maintained properly.
None | (N)2309.6.1.2.3 Stability of cylinders, containers and tanks. (Section deleted) |  |  | 2309.6.1.2.3 Stability of cylinders, containers and tanks. A method of rigidly supporting cylinders, containers or tanks used during the closed transfer system discharge or defueling of hydrogen shall be provided. The method shall provide not less than two points of support and shall be designed to resist lateral movement of the receiving cylinder, container or tank. The system shall be designed to resist movement of the receiver based on the highest gas-release velocity through valve orifices at the receiver's rated service pressure and volume. Supporting structures or appurtenances used to support recivers shall be constructed of noncombustible materials in accordance with the applicable building code. |  | Stabilty of cylinders is an operational issue with equipment, not construction. Vehicle hydrogen fuel containers can hold extremely high pressures, which, if released quickly, can produce large thrust forces that would propel the container like a rocket. Hydrogen does not liquefy at normal ambient temperatures; therefore, in order to hold the required amount of fuel on board the vehicle, the gaseous fuel must be compressed to extreme pressures of 3,000 to 5,000 psia (20 613 to 34 355 kPa).
None | (N)2309.6.1.2.4 Grounding and bonding. Grounding and bonding of cylinders, containers or tanks, and piping shall be maintained in accordance with the applicable building code. |  |  | 2309.6.1.2.4 Grounding and bonding. Cylinders, containers or tanks and piping systems used for defueling shall be bonded and grounded. Unless specifically approved otherwise in accordance with the applicable building code, structures or appurtenances used for supporting the cylinders, containers or tanks shall be grounded in accordance with NFPA 70. The valve of the vehicle storage tank shall be bonded with the defueling system prior to the commencement of discharge or defueling operations. |  | Grounding and bonding is an operational proceedure, not construction.
None | (N)2309.6.2 Repair of hydrogen piping. Piping systems containing hydrogen shall not be opened to the atmosphere for repair without first purging the piping with an inert gas to achieve 1% hydrogen or less by volume. |  |  | 2309.6.2 Repair of hydrogen piping. Piping systems containing hydrogen shall not be opened to the atmosphere for repair without first purging the piping with an inert gas to achieve 1%t hydrogen or less by volume. Defueling operations and exiting purge flow shall be vented in accordance with Section 2309.6.1.2. |  | Operational procedures, not construction. The proposal restores the last sentence referencing proper discharge. To prevent the release of flammable hydrogen gas to the atmosphere and to prevent an explosive hydrogen-air mixture (above 1-percent hydrogen based on the pipe volume) within system piping, this section requires that piping be purged with an inert gas before being disconnected and repaired.
2310.1 General. The construction of marine motor fuel-dispensing facilities shall be in accordance with the International Building Code and NFPA 30A. The storage of Class I, II or IIIA liquids at marine motor fuel-dispensing facilities shall be in accordance with this chapter and Chapter 57. | 2310.1 General. The construction of marine motor fuel-dispensing facilities shall be in accordance with this section and other applicable provisions of this code. |  |  | 2310.1 General. Marine motor fuel-dispensing facilities shall be maintained and remain in accordance with the applicable building code and NFPA 30A. The storage of Class I, II or IIIA liquids at marine motor fuel-dispensing facilities shall be maintained in accordance with this chapter and Chapter 57. |  | Scoping section regarding maintenance of motor fuel-dispensing faciltiies.
2310.2 Storage and handling. The storage and handling of Class I, II or IIIA liquids at marine motor fuel-dispensing facilities shall be in accordance with Sections 2310.2.1 through 2310.2.3. | (N)2310.2 Storage and handling. The storage and handling of Class I, II or IIIA liquids at marine motor fuel-dispensing facilities shall be maintained in accordance with the applicable building code. |  |  | 2310.2 Storage and handling. The storage and handling of Class I, II or IIIA liquids at marine motor vehicle fuel-dispensing facilities shall be in accordance with Sections 2310.2.1 through 2310.2.3. |  | There are no maintenance requirements in the building code.
2310.2.1 Class I, II or IIIA liquid storage. Class I, II or IIIA liquids stored inside of buildings used for marine motor fuel-dispensing facilities shall be stored in approved containers or portable tanks. Storage of Class I liquids shall not exceed 10 gallons (38 L). Exception: Storage in liquid storage rooms in accordance with Section 5704.3.7. | (N)2310.2.1 Class I, II or IIIA liquid storage. Class I, II or IIIA liquids stored inside of buildings used for marine motor fuel-dispensing facilities shall be stored in accordance with the applicable building code. |  |  | 2310.2.1 Class I, II or IIIA liquid storage. Unless otherwise approved in accordance with the applicable building code, Class I, II or IIIA liquids stored inside of buildings used for marine motor fuel-dispensing facilities shall be stored in approved containers or portable tanks. Storage of Class I liquids shall not exceed 10 gallons (38 L). Exception: Storage in liquid storage rooms in accordance with the applicable building code. |  | Maintenance of storage, not construction. There are no maintenance requirements in the building code.
2310.2.2 Class II or IIIA liquid storage and dispensing. Class II or IIIA liquids stored or dispensed inside of buildings used for marine motor fuel-dispensing facilities shall be stored in and dispensed from approved containers or portable tanks. Storage of Class II and IIIA liquids shall not exceed 120 gallons (454 L). | (N)2310.2.2 Class II or IIIA liquid storage and dispensing. Class II or IIIA liquids stored or dispensed inside of buildings used for marine motor fuel-dispensing facilities shall be stored in and dispensed in accordance with the applicable building code. |  |  | 2310.2.2 Class II or IIIA liquid storage and dispensing. Unless specifically approved otherwise in accordance with the applicable building code, Class II or IIIA liquids stored or dispensed inside of buildings used for marine motor vehicle fuel-dispensing facilities shall be stored in and dispensed from approved containers or portable tanks. Storage of Class II and IIIA liquids shall be maintained to not exceed 120 gallons (454 L). |  | There are no maintenance or operational requirements in the building code.
2310.2.3 Heating equipment. Heating equipment installed in Class I, II or IIIA liquid storage or dispensing areas shall comply with Section 2301.6. | (N)2310.2.3 Heating equipment. Heating equipment installed in Class I, II or IIIA liquid storage or dispensing areas shall be maintained in accordance with the applicable building code. |  |  | 2310.2.3 Heating equipment. Heating equipment installed in Class I, II or IIIA liquid storage or dispensing areas shall comply with Section 2301.6. |  | There are no maintenance requirements in the building code.
2310.3.3 Hoses and nozzles. Dispensing of Class I, II or IIIA liquids into the fuel tanks of marine craft shall be by means of an approved-type hose equipped with a listed automatic-closing nozzle without a latch-open device. Hoses used for dispensing or transferring Class I, II or IIIA liquids, when not in use, shall be reeled, racked or otherwise protected from mechanical damage. | (N)2310.3.3 Hoses and nozzles. Hoses and nozzles shall be maintained in accordance with the applicable building code. |  |  | 2310.3.3 Hoses and nozzles. Unless otherwise approved in accordance with the applicable building code, dispensing of Class I, II or IIIA liquids into the fuel tanks of marine craft shall be by means of an approved-type hose equpped with a listed automatic-closing nozzle without a latch-open device. Hoses used for dispensing or transferring Class I, II or IIIA liquids, when not in use, shall be reeled, racked or otherwise protected from mechanical damage. |  | Operational procedures, not construction. The automatic-closing-type nozzle is designed to operate with automotive-type fuel receivers. Many marine craft are not equipped with automotive-type fuel receivers with the vent line terminating in the receiver tube. It is the fuel returning in the vent line that shuts off the automatic-type nozzle. Therefore, the latch-open device must not be used on marine craft.
2310.3.5 Liquefied petroleum gas. Liquefied petroleum gas cylinders shall not be filled at marine motor fuel-dispensing facilities unless approved. Approved storage facilities for LP-gas cylinders shall be provided. See also Section 2307. | (N)2310.3.5 Liquefied petroleum gas. Liquefied petroleum gas cylinders shall not be filled at marine motor fuel-dispensing facilities unless approved. |  |  | 2310.3.5 Liquefied petroleum gas. Liquefied petroleum gas cylinders shall not be filled at marine motor fuel-dispensing facilities unless approved. Approved storage facilities fro LP-gas cyclinders shall be provided. See also Section 2307. |  | Operational proceedures for filling cylinders, not construction. Many marine vessels use LP-gas for heating and cooking. LP-gas cylinders may not be refilled at a marina, unless specifically approved. Section 2307 has requirements for dispensing LP-gas at motor fuel-dispensing facilities, and this section can be used in making the decision on whether to approve the dispensing operations of LP-gas at marinas.
2310.6 Fire protection. Fire protection features for marine motor fuel-dispensing facilities shall comply with Sections 2310.6.1 through 2310.6.4. | (N)2310.6 Fire protection. Fire protection features for marine motor fuel-dispensing facilities shall be maintained in accordance with the applicable building code. |  |  | 2310.6 Fire protection. Fire protection features for marine motor fuel-dispensing facilities shall be maintained in accordance with Sections 2310.6.1 through 2310.6.4 and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code.
2311.1 General. Repair garages shall comply with this section and the International Building Code. Repair garages for vehicles that use more than one type of fuel shall comply with the applicable provisions of this section for each type of fuel used. Where a repair garage also includes a motor fuel-dispensing facility, the fuel-dispensing operation shall comply with the requirements of this chapter for motor fuel-dispensing facilities. | 2311.1 General. Operation and maintenance of repair garages shall comply be in accordance with this section and other applicable provisions of this code. Repair garages for vehicles that use more than one type of fuel shall comply with the applicable provisions of this section for each type of fuel used. Where a repair garage includes a motor fueldispensing facility, the fuel-dispensing operation shall comply with the requirements of this chapter for motor fuel-dispensing facilities. |  |  | no change
2311.2 Storage and use of flammable and combustible liquids. The storage and use of flammable and combustible liquids in repair garages shall comply with Chapter 57 and Sections 2311.2.1 through 2311.2.4. | (N)2311.2 Storage and use of flammable and combustible liquids. The storage and use of flammable and combustible liquids in repair garages shall maintained in accordance with the applicable building code. |  |  | 2311.2 Storage and use of flammable and combustible liquids. The storage and use of flammable and combustible liquids in repair garages shall be maintained in accordance with Chapter 57 and Sections 2311.2.1 through 2311.2.4 and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code.
2311.2.3 Drainage and disposal of liquids and oil-soaked waste. Garage floor drains, where provided, shall drain to approved oil separators or traps discharging to a sewer in accordance with the International Plumbing Code. Contents of oil separators, traps and floor drainage systems shall be collected at sufficiently frequent intervals and removed from the premises to prevent oil from being carried into the sewers. | (N)2311.2.3 Drainage and disposal of liquids and oil soaked waste. Contents of oil separators, traps and floor drainage systems shall be collected at sufficiently frequent intervals and removed from the premises to prevent oil from being carried into the sewers. |  |  | no change
2311.3.1 Equipment. Appliances and equipment installed in a repair garage shall comply with the provisions of the International Building Code, the International Mechanical Code and NFPA 70. | (N)2311.3.1 Equipment. Appliances and equipment installed in a repair garage shall be maintained in accordance with the applicable building code. |  |  | 2311.3.1 Equipment. Appliances and equipment installed in a repair garage shall be maintained and the provisions NFPA 70, Chapter 6 of this code and remain in accordance with the applicable building code. |  | Maintenance of appliances and equipment. There are no maintenance requirements in the building code.
2311.4 Below-grade areas. Pits and below-grade work areas in repair garages shall comply with Sections 2311.4.1 through 2311.4.3. | (N)2311.4 Below-grade areas. Pits and below-grade work areas in repair garages shall be maintained in accordance with the applicable building code. |  |  | 2311.4 Below-grade areas. Pits and below-grade work areas in repair garages shall comply with Sections 2311.4.1 through 2311.4.3. |  | Scoping section only, there are no maintenance requirements in the building code.
2311.4.1 Construction. Pits and below-grade work areas shall be constructed in accordance with the International Building Code. | (N)2311.4.1 Construction. (Section deleted) |  |  | no change
2311.4.2 Means of egress. Pits and below-grade work areas shall be provided with means of egress in accordance with Chapter 10. | (N)2311.4.2 Means of egress. Means of egress for pits and below-grade work areas shall be maintained in accordance with the applicable building code. |  |  | 2311.4.2 Means of egress. Means of egress for pits and below-grade work areas shall be maintained in accordance with Chapter 10 and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code.
2311.4.3 Ventilation. Where Class I liquids or LP-gas are stored or used within a building having a basement or pit wherein flammable vapors could accumulate, the basement or pit shall be provided with mechanical ventilation in accordance with the International Mechanical Code, at a minimum rate of 11/2 cubic feet per minute per square foot (cfm/ft2) [0.008 m3/(s • m2)] to prevent the accumulation of flammable vapors. | (N)2311.4.3 Ventilation. Where Class I liquids or LP-gas are stored or used within a building having a basement or pit wherein flammable vapors could accumulate, the basement or pit mechanical ventilation, where provided, shall be maintained in accordance with the applicable building code. |  |  | 2311.4.3 Ventilation. Where Class I liquids or LP-gas are stored or used within a building having a basement or pit wherein flammable vapors could accumulate, the basement or pit shall maintain mechanical ventilation and remain in accordance with the applicable building code, to prevent the accumulation of flammable vapors. |  | There are no maintenance requirements in the building code. It is critical that a ventilation system must be operated and maintained in any belowgrade area where flammable and combustible vapors might accumulate. The ventilation system must be in operation any time the repair garage is open for business, if a vehicle is left parked over the pit when the garage is closed for business or anytime there is a chance that vapors may accumulate in the belowgrade area. It is never ok to allow operations which permit the accumulation of flammable vapors.
2311.7.1 Ventilation. Repair garages used for the repair of natural gas- or hydrogen-fueled vehicles shall be provided with an approved mechanical ventilation system. The mechanical ventilation system shall be in accordance with the International Mechanical Code and Sections 2311.7.1.1 and 2311.7.1.2. Exception: Repair garages with natural ventilation when approved. | (N)2311.7.1 Ventilation. Ventilation required for repair garages used for the repair of natural gas-fueled vehicles or hydrogenfueled vehicles shall be maintained in accordance with the applicable building code. Exception: Repair garages with natural ventilation when approved. |  |  | 2311.7.1 Ventilation. Repair garages used for the repair of natural gas- or hydrogen-fueled vehicles shall maintain an approved mechanical ventilation system. The mechanical ventilation system shall remain in accordance with the applicable building code and Section 2311.7.1.2. Exception: Repair garages with natural ventilation when approved. |  | There are no maintenance requiremetns in the building code. This proposal also restores reference to an additioanl operational code section.
2311.7.1.1 Design. Indoor locations shall be ventilated utilizing air supply inlets and exhaust outlets arranged to provide uniform air movement to the extent practical. Inlets shall be uniformly arranged on exterior walls near floor level. Outlets shall be located at the high point of the room in exterior walls or the roof. Ventilation shall be by a continuous mechanical ventilation system or by a mechanical ventilation system activated by a continuously monitoring natural gas detection system or, for hydrogen, a continuously monitoring flammable gas detection system, each activating at a gas concentration of not more than 25 percent of the lower flammable limit (LFL). In all cases, the system shall shut down the fueling system in the event of failure of the ventilation system. The ventilation rate shall be at least 1 cubic foot per minute per 12 cubic feet [0.00139 m3 × (s • m3)] of room volume. | (N)2311.7.1.1 Design. (Section deleted) |  |  | no change
2311.7.1.2 Operation. The mechanical ventilation system shall operate continuously. Exceptions: 1.Mechanical ventilation systems that are interlocked with a gas detection system designed in accordance with Sections 2311.7.2 through 2311.7.2.3. 2.Mechanical ventilation systems in repair garages that are used only for repair of vehicles fueled by liquid fuels or odorized gases, such as CNG, where the ventilation system is electrically interlocked with the lighting circuit. | (N)2311.7.1.2 Operation. The mechanical ventilation system shall be maintained in accordance with the applicable building code. |  |  | (N)2311.7.1.2 Operation. The mechanical ventilation system shall be maintained to operate continuously unless otherwise approved in accordance with the applicable building code. Exceptions: 1.Mechanical ventilation systems that are interlocked with a gas detection system designed in accordance with Sections 2311.7.2 through 2311.7.2.3. 2.Mechanical ventilation systems in repair garages that are used only for repair of vehicles fueled by liquid fuels or odorized gases, such as CNG, where the ventilation system is electrically interlocked with the lighting circuit. |  | There are no maintenance requirements in the building code. The intent of this operational requirement is to prevent the accumulation of lighter-than-air gases inside vehicle repair garages through continuous operation of ventilation. The proposal retains the exceptions to recognize situations where continuous operation would not be required but are not construction requirements.
2311.7.2 Gas detection system. Repair garages used for repair of vehicles fueled by nonodorized gases, such as hydrogen and nonodorized LNG, shall be provided with a flammable gas detection system. | (N)2311.7.2 Gas detection system. Gas detection systems required for repair garages used for repair of vehicles fueled by nonodorized gases, including hydrogen and nonodorized liquefied natural gas, shall be maintained in accordance with the applicable building code. |  |  | 2311.7.2 Repair garages shall be used for repair of vehicles fueled by nonodorized gases including, but not limited to, hydrogen and nonodorized LNG, only where provided with a flammable gas detection system in accordance with the applicable building code. Gas detection systems shall be maintained in accordance with Chapter 9 and Section 2311.7.2.1. |  | There are no maintenance requirements in the building code. Some gases contain additives that produce pungent odors for easy recognition. If the vehicle contains fuel systems that do not use these odorized gases, must be repaired at an appropriate facility. This is not construction but rather appropriate use and operation.
2311.7.2.1 System design. The flammable gas detection system shall be listed or approved and shall be calibrated to the types of fuels or gases used by vehicles to be repaired. The gas detection system shall be designed to activate when the level of flammable gas exceeds 25 percent of the lower flammable limit (LFL). Gas detection shall also be provided in lubrication or chassis service pits of repair garages used for repairing nonodorized LNG-fueled vehicles. | (N)2311.7.2.1 System design. (Section deleted) |  |  | 2311.7.2.1 System calibration. The flammable gas detection system shall remain calibrated to the types of fuels or gases used by vehicles to be repaired. Unless otherwise approved by the applicable building code, the gas detection system shall activate when the level of flammable gas exceeds 25 percent of the lower flammable limit (LFL). |  | It is critical that a gas detection systems be maintained properly calibrated to activate upon detection of a flammable vapor environment. This section identifies that flammable vapor thershold as 25% of the LFL.
2311.7.2.1.1 Gas detection system components. Gas detection system control units shall be listed and labeled in accordance with UL 864 or UL 2017. Gas detectors shall be listed and labeled in accordance with UL 2075 for use with the gases and vapors being detected. | (N)2311.7.2.1.1 Gas detection system components. (Section deleted) |  |  | no change
2311.7.2.2 Operation. Activation of the gas detection system shall result in all the following: 1.Initiation of distinct audible and visual alarm signals in the repair garage. 2.Deactivation of all heating systems located in the repair garage. 3.Activation of the mechanical ventilation system, when the system is interlocked with gas detection. | (N)2311.7.2.2 Operation. (Section deleted) |  |  | no change
2311.7.2.3 Failure of the gas detection system. Failure of the gas detection system shall result in the deactivation of the heating system, activation of the mechanical ventilation system and where the system is interlocked with gas detection and causes a trouble signal to sound in an approved location. | (N)2311.7.2.3 Failure of the gas detection system. (Section deleted) |  |  | no change

## Ch24 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
2401.3 Permits. Permits shall be required as set forth in Section 107.2. | 2401.3 Permits. Permits shall be required as set forth in Section 107.2 |  |  | No change
2403.2.1 Electrical wiring and equipment. Electrical wiring and equipment shall comply with this chapter and NFPA 70. | (N)2403.2.1 Electrical wiring and equipment. Electrical wiring and equipment shall be maintained in accordance with the applicable building code |  | add the words 'and the International Fire Code" because the building code does not address this | 2403.2.1 Electrical wiring and equipment. Electrical wiring and equipment shall be maintained in accordance with this chapter, chapter 6 and NFPA 70.
2403.2.1.1 Flammable vapor areas. Electrical wiring and equipment in flammable vapor areas shall be of an explosionproof type approved for use in such hazardous locations. Such areas shall be considered to be Class I, Division 1 or Class II, Division 1 hazardous locations in accordance with NFPA 70. | (N)2403.2.1.1 Flammable vapor areas. Electrical wiring and equipment in flammable vapor areas shall be of an explosion proof type approved for use in such hazardous locations and maintained in accordance with the applicable building code. |  |  | 2403.2.1.1 Flammable vapor areas. Electrical wiring and equipment in flammable vapor areas shall be of an explosion proof type approved for use in such hazardous locations as classified by the applicable building code and maintained in accordance with NFPA 70, and chapter 6.
2403.2.1.2 Areas subject to deposits of residues. Electrical equipment, flammable vapor areas or drying operations that are subject to splashing or dripping of liquids shall be specifically approved for locations containing deposits of readily ignitable residue and explosive vapors. Exceptions: 1.This provision shall not apply to wiring in rigid conduit, threaded boxes or fittings not containing taps, splices or terminal connections. 2.This provision shall not apply to electrostatic equipment allowed by Section 2407. In resin application areas, electrical wiring and equipment that is subject to deposits of combustible residues shall be listed for such exposure and shall be installed as required for hazardous (classified) locations. Electrical wiring and equipment not subject to deposits of combustible residues shall be installed as required for ordinary hazard locations. | (N)2403.2.1.2 Areas subject to deposits of residues. Flammable vapor areas or drying operations that are subject to splashing or dripping of liquids shall be specifically approved for locations containing deposits of readily ignitable residue and explosive vapors. |  | use 2012 language | 2403.2.1.2 Areas subject to deposits of residues. Electrical equipment, flammable vapor areas or drying operations that are subject to splashing or dripping of liquids shall be specifically approved for locations containing deposits of readily ignitable residue and explosive vapors. Exceptions: 1.This provision shall not apply to wiring in rigid conduit, threaded boxes or fittings not containing taps, splices or terminal connections. 2.This provision shall not apply to electrostatic equipment allowed by Section 2407. In resin application areas, electrical wiring and equipment that is subject to deposits of combustible residues shall be listed for such exposure and shall be installed as required for hazardous (classified) locations. Electrical wiring and equipment not subject to deposits of combustible residues shall be installed as required for ordinary hazard locations.
2403.2.1.3 Areas adjacent to spray booths. Electrical wiring and equipment located outside of, but within 5 feet (1524 mm) horizontally and 3 feet (914 mm) vertically of openings in a spray booth or a spray room, shall be approved for Class I, Division 2 or Class II, Division 2 hazardous locations, whichever is applicable. | (N)2403.2.1.3 Areas adjacent to spray booths. Electrical wiring and equipment located outside of, but within 5 feet (1524 mm) horizontally and 3 feet (914 mm) vertically of, openings in a spray booth or a spray room shall be maintained in accordance with the applicable building code. |  | use 2012 language. electrical equipment not requireing a building permit may be placed there | 2403.2.1.3 Areas adjacent to spray booths. Electrical wiring and equipment located outside of, but within 5 feet (1524 mm) horizontally and 3 feet (914 mm) vertically of openings in a spray booth or a spray room, shall be approved for hazardous locations in accordance with the applicable building code and maintained in accordance with NFPA 70 and Chapter 6.
2403.2.5 Grounding. Metal parts of spray booths, exhaust ducts and piping systems conveying Class I or II liquids shall be electrically grounded in accordance with NFPA 70. Metallic parts located in resin application areas, including but not limited to exhaust ducts, ventilation fans, spray application equipment, workpieces and piping, shall be electrically grounded. | (N)2403.2.5 Grounding. The grounding of metal parts of spray booths, exhaust ducts, and piping systems conveying Class I or II liquids shall be maintained in accordance with the applicable building code |  | Use 2012 language. The USBC does not address grounding and refers back to the IFC which does. | 2403.2.5 Grounding. Metal parts of spray booths, exhaust ducts and piping systems conveying Class I or II liquids shall be electrically grounded in accordance with NFPA 70. Metallic parts located in resin application areas, including but not limited to exhaust ducts, ventilation fans, spray application equipment, workpieces and piping, shall be electrically grounded.
2404.1 General. The application of flammable or combustible liquids by means of spray apparatus in continuous or intermittent processes shall be in accordance with the requirements of Sections 2403 and 2404.2 through 2404.9.4. | (N)2404.1 General. The application of flammable or combustible liquids by means of spray apparatus in continuous or intermittent processes shall be in accordance with the requirements of Sections 2403 and 2404. |  |  | no change
2404.2 Location of spray-finishing operations. Spray finishing operations conducted in buildings used for Group A, E, I or R occupancies shall be located in a spray room protected with an approved automatic sprinkler system installed in accordance with Section 903.3.1.1 and separated vertically and horizontally from other areas in accordance with the International Building Code. In other occupancies, spray-finishing operations shall be conducted in a spray room, spray booth or spraying space approved for such use. Exceptions: 1.Automobile undercoating spray operations and spray-on automotive lining operations conducted in areas with approved natural or mechanical ventilation shall be exempt from the provisions of Section 2404 when approved and where utilizing Class IIIA or IIIB combustible liquids. 2.In buildings other than Group A, E, I or R occupancies, approved limited spraying space in accordance with Section 2404.9. 3.Resin application areas used for manufacturing of reinforced plastics complying with Section 2409 shall not be required to be located in a spray room, spray booth or spraying space. | (N)2404.2 Location of spray-finishing operations. (Section deleted) |  | Location of spray finishing operations. Spray finishing operations shall not be conducted in buildings used for group A,E,I, or R Exception- buildings that are provided fire protection system in accordance with the USBC | 2404.2 Location of spray-finishing operations. Spray finishing operations shall not be conducted in buildings used for Group A, E, I or R occupancies except where approved in accordance with the applicable building code. In other occupancies, spray-finishing operations shall be conducted in a spray room, spray booth or spraying space approved for such use. Exceptions: 1.Automobile undercoating spray operations and spray-on automotive lining operations conducted in areas with approved natural or mechanical ventilation shall be exempt from the provisions of Section 2404 when approved and where utilizing Class IIIA or IIIB combustible liquids. 2.In buildings other than Group A, E, I or R occupancies, approved limited spraying space in accordance with Section 2404.9. 3.Resin application areas used for manufacturing of reinforced plastics complying with Section 2409 shall not be required to be located in a spray room, spray booth or spraying space.
2404.3 Design and construction. Design and construction of spray rooms, spray booths and spray spaces shall be in accordance with Sections 2404.3 through 2404.3.3.1. | (N)2404.3 Design and construction. (Section deleted) |  | Design and construction of spray booths shall be in accordance with the USBC | 2404.3 Design and construction. Design and construction of spray rooms, spray booths and spray spaces shall be in accordance with the applicable building code and Sections 2404.3 through 2404.3.3.1.
2404.3.1 Spray rooms. Spray rooms shall be constructed and designed in accordance with this section and the International Building Code, and shall comply with Sections 2404.4 through 2404.8. | (N)2404.3.1 Spray rooms. Spray rooms shall be maintained in accordance with the applicable building code. |  | Design and construction of spray rooms shall be in accordance with the USBC | 2404.3.1 Spray rooms. Spray rooms shall be maintained in accordance with this section and remain in accordance with the applicable building code.
2404.3.1.1 Floor. Combustible floor construction in spray rooms shall be covered by approved, noncombustible, nonsparking material, except where combustible coverings, including but not limited to thin paper or plastic and strippable coatings, are utilized over noncombustible materials to facilitate cleaning operations in spray rooms. | (N)2404.3.1.1 Floor. Combustible floor construction in spray rooms shall be maintained in accordance with the applicable building code. |  | Use 2012 language. Its not construction releated. it maintenance and operational. This addresses what the floor is made of | 2404.3.1.1 Floor. Combustible floor construction in spray rooms shall be covered by approved, noncombustible, nonsparking material, except where combustible coverings, including but not limited to thin paper or plastic and strippable coatings, are utilized over noncombustible materials to facilitate cleaning operations in spray rooms.
2404.3.2 Spray booths. The design and construction of spray booths shall be in accordance with Sections 2404.3.2.1 through 2404.3.2.6, Sections 2404.4 through 2404.8 and NFPA 33. | (N)2404.3.2 Spray booths. Spray booths shall be maintained in accordance with the applicable building code. |  | Spray booths shall be constructed in accordance with the appicable building code. Or delete | 2404.3.2 Spray booths. The design and construction of spray booths shall be in accordance with the applicable building code and maintained in accordance with section 2404.3.2.2 through 2403.3.2.5 and 2304 through 2304.8 and NFPA 33.
2404.3.2.1 Construction. Spray booths shall be constructed of approved noncombustible materials. Aluminum shall not be used. Where walls or ceiling assemblies are constructed of sheet metal, single-skin assemblies shall be no thinner than 0.0478 inch (18 gage) (1.2 mm) and each sheet of double-skin assemblies shall be no thinner than 0.0359 inch (20 gage) (0.9 mm). Structural sections of spray booths are allowed to be sealed with latex-based or similar caulks and sealants. | (N)2404.3.2.1 Construction. (Section deleted) |  |  | No change
2404.3.2.2 Surfaces. The interior surfaces of spray booths shall be smooth; shall be constructed so as to permit the free passage of exhaust air from all parts of the interior, and to facilitate washing and cleaning; and shall be designed to confine residues within the booth. Aluminum shall not be used. | (N)2404.3.2.2 Surfaces. The interior surfaces of spray booths shall be maintained in accordance with the applicable building code. |  | Use 2012 language. Its not construction releated. it maintenance and operational | 2404.3.2.2 Surfaces. The interior surfaces of spray booths shall be smooth; shall be maintained so as to permit the free passage of exhaust air from all parts of the interior, and to facilitate washing and cleaning; and shall be maintained to confine residues within the booth. Aluminum shall not be used unless approved by the applicable building code.
2404.3.2.3 Floor. Combustible floor construction in spray booths shall be covered by approved, noncombustible, nonsparking material, except where combustible coverings, including but not limited to thin paper or plastic and strippable coatings, are utilized over noncombustible materials to facilitate cleaning operations in spray booths. | (N)2404.3.2.3 Floor. Combustible floor construction in spray booths shall be maintained in accordance with the applicable building code. |  | Is floor covering a building code item or an operational item? The 2012 has guidance for combustible coverings. | 2404.3.2.3 Floor covering. Combustible floor construction in spray booths shall be covered by approved, noncombustible, nonsparking material, except where combustible coverings, including but not limited to thin paper or plastic and strippable coatings, are utilized over noncombustible materials to facilitate cleaning operations in spray booths.
2404.3.2.4 Means of egress. Means of egress shall be provided in accordance with Chapter 10. Exception: Means of egress doors from premanufactured spray booths shall not be less than 30 inches (762 mm) in width by 80 inches (2032 mm) in height. | (N)2404.3.2.4 Means of egress. Means of egress shall be maintained in accordance with the applicable building code. |  | 2404.3.2.4 Means of egress. Means of egress shall be maintained in accordance with Chapter 10 and remain in accordance with the applicable building code. | (N)2404.3.2.4 Means of egress. Means of egress shall be maintained in accordance with the applicable building code and Chapter 10.
2404.3.2.5 Clear space. Spray booths shall be installed so that all parts of the booth are readily accessible for cleaning. A clear space of not less than 3 feet (914 mm) shall be maintained on all sides of the spray booth. This clear space shall be kept free of any storage or combustible construction. Exceptions: 1.This requirement shall not prohibit locating a spray booth closer than 3 feet (914 mm) to or directly against an interior partition, wall or floor/ceiling assembly that has a fire-resistance rating of not less than 1 hour, provided the spray booth can be adequately maintained and cleaned. 2.This requirement shall not prohibit locating a spray booth closer than 3 feet (914 mm) to an exterior wall or a roof assembly, provided the wall or roof is constructed of noncombustible material and the spray booth can be adequately maintained and cleaned. | (N)2404.3.2.5 Clear space. A clear space of not less than 3 feet (914 mm) shall be maintained on all sides of the spray booth. This clear space shall be kept free of any storage or combustible construction. |  |  | 2404.3.2.5 Clear space. Spray booths shall be installed so that all parts of the booth are readily accessible for cleaning. A clear space of not less than 3 feet (914 mm) shall be maintained on all sides of the spray booth. This clear space shall be kept free of any storage or combustible construction. Exceptions: If approved in accordance with the applicable building code, 1.This requirement shall not prohibit locating a spray booth closer than 3 feet (914 mm) to or directly against an interior partition, wall or floor/ceiling assembly that has a fire-resistance rating of not less than 1 hour, provided the spray booth can be adequately maintained and cleaned. 2.This requirement shall not prohibit locating a spray booth closer than 3 feet (914 mm) to an exterior wall or a roof assembly, provided the wall or roof is constructed of noncombustible material and the spray booth can be adequately maintained and cleaned.
2404.3.2.6 Size.he aggregate area of spray booths in a building shall not exceed the lesser of 10 percent of the area of any floor of a building or the basic area allowed for a Group H-2 occupancy without area increases, as set forth in the International Building Code. The area of an individual spray booth in a building shall not exceed the lesser of the aggregate size limit or 1,500 square feet (139 m2). Exception: One individual booth not exceeding 500 square feet (46 m2). | (N)2404.3.2.6 Size. (Section deleted) |  |  | no change
2404.3.3 Spraying spaces. Spraying spaces shall be designed and constructed in accordance with the International Building Code, and Section 2404.3.3.1 and Sections 2404.4 through 2404.8 of this code. | (N)2404.3.3 Spraying spaces. Spraying spaces shall be maintained in accordance with the applicable building code. |  | Change "maintained" to read "constructed. Maintained creates confusion on the "operational maintenance" of a spray space | 2404.3.3 Spraying spaces. Spraying spaces shall be designed and constructed in accordance with the applicalbe building code and maintained in accordance with Section 2404.3.3.1 and Sections 2404.4 through 2404.8 of this code.
2404.3.3.1 Floor.Combustible floor construction in spraying spaces shall be covered by approved, noncombustible, nonsparking material, except where combustible coverings, such as thin paper or plastic and strippable coatings, are utilized over noncombustible materials to facilitate cleaning operations in spraying spaces. | (N)2404.3.3.1 Floor. Combustible floor construction in spraying spaces shall be maintained in accordance with the applicable building code. |  | use 2012 language. It is maintenance related not construction | 2404.3.3.1 Floor covering.Combustible floor construction in spraying spaces shall be covered by approved, noncombustible, nonsparking material, except where combustible coverings, such as thin paper or plastic and strippable coatings, are utilized over noncombustible materials to facilitate cleaning operations in spraying spaces.
2404.4 Fire protection. Spray booths and spray rooms shall be protected by an approved automatic fire-extinguishing system complying with Chapter 9. Protection shall also extend to exhaust plenums, exhaust ducts and both sides of dry filters when such filters are used | (N)2404.4 Fire protection. Automatic fireextinguishing systems provided for spray booths shall be maintained in accordance with the applicable building code. |  | use 2012 language- the building code makes no refrence to the maintenance of fire protection systems | 2404.4 Fire protection. Unless otherwise permitted by the applicable building code, spray booths and spray rooms shall be protected by an approved automatic fire-extinguishing system complying with the requirements of the applicable building code and maintained in accordance with Chapter 9. |  | 2404.4 Fire protection. Automatic fire extinguishing systems provided for spray booths shall be maintained in accordance with Chapter 9 and remain in accordanc with the applicable building code.
2404.6.2.1 Glass panels. Panels for luminaires or for observation shall be of heat-treated glass, wired glass or hammered wire glass and shall be sealed to confine vapors, mists, residues, dusts and deposits to the flammable vapor area. Panels for luminaires shall be separated from the luminaire to prevent the surface temperature of the panel from exceeding 200°F (93°C). | (N)2404.6.2.1 Glass panels. Panels for luminaires or for observation shall be maintained in accordance with the applicable building code. |  | No change? Building Code 307.1.1 references the IFC | 2404.6.2.1 Glass panels. Panels for luminaires or for observation shall maintain seals to confine vapors, mists, residues, dusts and deposits to the flammable vapor area. Panels for luminaires shall be separated from the luminaire to prevent the surface temperature of the panel from exceeding 200°F (93°C). |  | 1978 BOCA: F-702.3.7 Illumination: When spraying areas are illuminated through glass panels or other transparent materials, only fixed lighting units shall be used as a source of illumination. Panels shall effectively isolate the spraying area from the area in which the lighting unit is located and shall be of noncombustible material of such a nature or so protected that breakage will be unlikely. Panels shall be so arranged that normal accumulations of residue on the exposed surface of the panel will not be raised to a dangerous temperature
2404.6.2.2 Exterior luminaires. Luminaires attached to the walls or ceilings of a flammable vapor area, but outside of any classified area and separated from the flammable vapor areas by vapor-tight glass panels, shall be suitable for use in ordinary hazard locations. Such luminaires shall be serviced from outside the flammable vapor areas. | (N)2404.6.2.2 Exterior luminaires. Luminaires attached to the walls or ceilings of a flammable vapor area, but outside of any classified area and separated from the flammable vapor areas by vapor-tight glass panels, shall be maintained in accordance with the applicable building code. |  | add the words- and the International Fire since thats what the building code refers to. | 2404.6.2.2 Exterior luminaires. Luminaires attached to the walls or ceilings of a flammable vapor area, but outside of any classified area and separated from the flammable vapor areas by vapor-tight glass panels, shall be suitable for use in ordinary hazard locations. Such luminaires shall be serviced from outside the flammable vapor areas.
2404.6.2.3 Integral luminaires. Luminaires that are an integral part of the walls or ceiling of a flammable vapor area are allowed to be separated from the flammable vapor area by glass panels that are an integral part of the luminaire. Such luminaires shall be listed for use in Class I, Division 2 or Class II, Division 2 locations, whichever is applicable, and also shall be suitable for accumulations of deposits of combustible residues. Such luminaires are allowed to be serviced from inside the flammable vapor area. | (N)2404.6.2.3 Integral luminaires. Luminaires that are an integral part of the walls or ceiling of a flammable vapor area are allowed to be separated from the flammable vapor area by glass panels that are an integral part of the luminaire. Such luminaires shall be maintained in accordance with the applicable building code. |  | add the words- and the International Fire since thats what the building code refers to. | 2404.6.2.3 Integral luminaires. Luminaires that are an integral part of the walls or ceiling of a flammable vapor area are allowed to be separated from the flammable vapor area by glass panels that are an integral part of the luminaire. Such luminaires shall be used only if listed for use in hazardous locations in accordance with the applicable building code and also shall be suitable for accumulations of deposits of combustible residues. Such luminaires are allowed to be serviced from inside the flammable vapor area. |  | Delete?
2404.7 Ventilation. Mechanical ventilation of flammable vapor areas shall be provided in accordance with Section 502.7 of the International Mechanical Code. | (N)2404.7 Ventilation. Mechanical ventilation of flammable vapor areas shall be maintained in accordance with the applicable building code |  | 2404.7 Ventilation. Mechanical ventilation of flammable vapor areas shall be maintained in accordance with this section and remain in accordance with the applicable building code | 2404.7 Ventilation. Mechanical ventilation of flammable vapor areas shall be maintained in accordance with this section and remain in accordance with the applicable building code.
2404.7.1 Operation. Mechanical ventilation shall be kept in operation at all times while spraying operations are being conducted and for a sufficient time thereafter to allow vapors from drying coated articles and finishing material residue to be exhausted. Spraying equipment shall be interlocked with the ventilation of the flammable vapor areas such that spraying operations cannot be conducted unless the ventilation system is in operation. | (N)2404.7.1 Operation. Where provided, mechanical ventilation shall be kept in operation at all times while spraying operations are being conducted and for a sufficient time thereafter to allow vapors from drying coated articles and finishing material residue to be exhausted.
2404.7.2 Recirculation. Air exhausted from spraying operations shall not be recirculated. Exceptions: 1.Air exhausted from spraying operations is allowed to be recirculated as makeup air for unmanned spray operations, provided that: 1.1.The solid particulate has been removed. 1.2.The vapor concentration is less than 25 percent of the LFL. 1.3.Approved equipment is used to monitor the vapor concentration. 1.4.When the vapor concentration exceeds 25 percent of the LFL, the following shall occur: a.An alarm shall sound; and b.Spray operations shall automatically shut down. 1.5.In the event of shutdown of the vapor concentration monitor, 100 percent of the air volume specified in Section 510 of the International Mechanical Code is automatically exhausted. 2.Air exhausted from spraying operations is allowed to be recirculated as makeup air to manned spraying operations where all of the conditions provided in Exception 1 are included in the installation and documents have been prepared to show that the installation does not pose a life safety hazard to personnel inside the spray booth, spraying space or spray room. | (N)2404.7.2 Recirculation. (Section deleted) |  | use 2012 language- this is operational not constructions related | 2404.7.2 Recirculation. Air exhausted from spraying operations shall not be recirculated. Exceptions: 1.Air exhausted from spraying operations is allowed to be recirculated as makeup air for unmanned spray operations, provided that: 1.1.The solid particulate has been removed. 1.2.The vapor concentration is less than 25 percent of the LFL. 1.3.Approved equipment is used to monitor the vapor concentration. 1.4.When the vapor concentration exceeds 25 percent of the LFL, the following shall occur: a.An alarm shall sound; and b.Spray operations shall automatically shut down. 1.5.In the event of shutdown of the vapor concentration monitor, 100 percent of the air volume specified in Section 510 of the International Mechanical Code is automatically exhausted.
2404.7.3 Air velocity. Ventilation systems shall be designed, installed and maintained such that the average air velocity over the open face of the booth, or booth cross section in the direction of airflow during spraying operations, shall not be less than 100 feet per minute (0.51 m/s). | (N)2404.7.3 Air velocity. The required air velocity for ventilation systems shall be maintained in accordance with the applicable building code. |  |  | no change
None | (N)2404.7.3.1 Open-face or open-front spray booth. For spray application operations conducted in an open-face or open-front spray booth, the ventilation system shall be maintained in accordance with the applicable building code. |  | add the words- and the International Fire Code because its not addressed in the building code. | 2404.7.3.1 Open-face or open-front spray booth. For spray application operations conducted in an open-face or open-front spray booth, the ventilation system air velocity shall be maintained in accordance with the requirements of the applicable building code.
None | (N)2404.7.3.2 Enclosed spray booth or spray room with openings for product conveyance. For spray application operations conducted in an enclosed spray booth or spray room with openings for product conveyance, the ventilation system shall be maintained in accordance with the applicable building code. |  | add the words- and the International Fire Code because its not addressed in the building code. | 2404.7.3.2 Enclosed spray booth or spray room with openings for product conveyance. For spray application operations conducted in an enclosed spray booth or spray room with openings for product conveyance, the ventilation system air velocity shall be maintained in accordance with the requirements of the applicable building code.
2404.7.5 Independent ducts. Each spray booth and spray room shall have an independent exhaust duct system discharging to the outside. Exceptions: 1.Multiple spray booths having a combined frontal area of 18 square feet (1.67 m2) or less are allowed to have a common exhaust when identical spray finishing material is used in each booth. If more than one fan serves one booth, fans shall be interconnected such that all fans will operate simultaneously. 2.Where treatment of exhaust is necessary for air pollution control or for energy conservation, ducts shall be allowed to be manifolded if all of the following conditions are met: 2.1.The sprayed materials used are compatible and will not react or cause ignition of the residue in the ducts. 2.2.Nitrocellulose-based finishing material shall not be used. 2.3.A filtering system shall be provided to reduce the amount of overspray carried into the duct manifold. 2.4.Automatic sprinkler protection shall be provided at the junction of each booth exhaust with the manifold, in addition to the protection required by this chapter. | (N)2404.7.5 Independent ducts. (Section deleted) |  | construction? | no change
2404.7.6 Termination point. The termination point for exhaust ducts discharging to the atmosphere shall not be less than the following distances: 1.Ducts conveying explosive or flammable vapors, fumes or dusts: 30 feet (9144 mm) from the lot line; 10 feet (3048 mm) from openings into the building; 6 feet (1829 mm) from exterior walls and roofs; 30 feet (9144 mm) from combustible walls or openings into the building that are in the direction of the exhaust discharge; 10 feet (3048 mm) above adjoining grade. 2.Other product-conveying outlets: 10 feet (3048 mm) from the lot line; 3 feet (914 mm) from exterior walls and roofs; 10 feet (3048 mm) from openings into the building; 10 feet (3048 mm) above adjoining grade. | (N)2404.7.6 Termination point. The termination point for exhaust ducts discharging to the atmosphere shall be maintained in accordance with the applicable building code. |  |  | (N)2404.7.6 Termination point. The termination point for exhaust ducts discharging to the atmosphere shall remain in accordance with the applicable building code.
2404.7.7 Fan motors and belts. Electric motors driving exhaust fans shall not be placed inside booths or ducts. Fan rotating elements shall be nonferrous or nonsparking or the casing shall consist of, or be lined with, such material. Belts shall not enter the duct or booth unless the belt and pulley within the duct are tightly enclosed. | 2404.7.7 Fan motors and belts. Electric motors driving exhaust fans shall not be placed inside booths or ducts, unless approved. Fan rotating elements shall be nonferrous or nonsparking or the casing shall consist of, or be lined with, such material. Belts shall not enter the duct or booth unless the belt and pulley within the duct are tightly enclosed. |  |  | no change
2404.7.8 Filters. Air intake filters that are part of a wall or ceiling assembly shall be listed as Class I or II in accordance with UL 900. Exhaust filters shall be required. | (N)2404.7.8 Filters. Air intake filters that are part of a wall or ceiling assembly shall be maintained. |  |  | 2404.7.8 Filters. Air intake filters that are part of a wall or ceiling assembly shall be listed as Class I or II in accordance with UL 900. Exhaust filters shall be required.
2404.7.8.1 Supports. Supports and holders for filters shall be constructed of noncombustible materials. | (N)2404.7.8.1 Supports. Supports and holders for filters shall be maintained. |  | use 2012 language. the word constructed is intended to mean "made of" not building construction | 2404.7.8.1 Supports. Supports and holders for filters shall be maintained as noncombustible materials unless otherwise approved by the applicable building code.
2404.7.8.3 Maintaining air velocity. Visible gauges, audible alarms or pressure-activated devices shall be installed to indicate or ensure that the required air velocity is maintained. | (N)2404.7.8.3 Maintaining air velocity. The required air velocity shall be maintained in accordance with the applicable building code. |  | use 2012 language- this is not addressed in the buidling code and is not construction related | 2404.7.8.3 Maintaining air velocity. Where provided, visible gauges, audible alarms or pressure-activated devices shall be maintained to indicate or ensure that the required air velocity is maintained.
2404.7.8.4 Filter rolls. Spray booths equipped with a filter roll that is automatically advanced when the air velocity is reduced to less than 100 feet per minute (0.51 m/s) shall be arranged to shut down the spraying operation if the filter roll fails to advance automatically. | (N)2404.7.8.4 Filter rolls. Filter rolls for spray booths shall be maintained in accordance with applicable building code. |  | and the words "and International Fire Code" because the building code does not asddress this | 2404.7.8.4 Filter rolls. Unless otherwise permitted by the applicable building code, where spray booths are equipped with a filter roll that is automatically advanced it shall be arranged to shut down the spraying operation if the filter roll fails to advance automatically.
2404.7.8.7 Waterwash spray booths. Waterwash spray booths shall be of an approved design so as to prevent excessive accumulation of deposits in ducts and residue at duct outlets. Such booths shall be arranged so that air and overspray are drawn through a continuously flowing water curtain before entering an exhaust duct to the building exterior. | (N)2404.7.8.7 Waterwash spray booths. Waterwash spray booths shall be maintained in accordance with the applicable building code |  | and the words "and International Fire Code" because the building code does not address this | 2404.7.8.7 Waterwash spray booths. Waterwash spray booths shall be maintained so as to prevent excessive accumulation of deposits in ducts and residue at duct outlets. Such booths shall be maintained so that air and overspray are drawn through a continuously flowing water curtain before entering an exhaust duct to the building exterior.
2404.8 Interlocks. Interlocks for spray application finishes shall be in accordance with Sections 2404.8.1 through 2404.8.2. | (N)2404.8 Interlocks. Interlocks for spray application finishes shall be maintained in accordance with the applicable building code. |  | and the words "and International Fire Code" because the building code does not address this | (N)2404.8 Interlocks. Interlocks for spray application finishes shall be maintained fully operational and remain in accordance with the applicable building code.
2404.8.1 Automated spray application operations. Where protecting automated spray application operations, automatic fire-extinguishing systems shall be equipped with an approved interlock feature that will, upon discharge of the system, automatically stop the spraying operations and workpiece conveyors into and out of the flammable vapor areas. Where the building is equipped with a fire alarm system, discharge of the automatic fire-extinguishing system shall also activate the building alarm notification appliances. | (N)2404.8.1 Automated spray application operations. (Section deleted) |  | Delete? | use 2012 language and add "in accordance with the USBC"
2404.8.1.1 Alarm station. A manual fire alarm and emergency system shutdown station shall be installed to serve each flammable vapor area. When activated, the station shall accomplish the functions indicated in Section 2404.8.1. | (N)2404.8.1.1 Alarm station. Where required, a manual fire alarm and emergency system shutdown station shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | (N)2404.8.1.1 Alarm station. Where required, a manual fire alarm and emergency system shutdown station shall be maintained accessible, fully operational and remain in accordance with the applicable building code.
2404.8.1.2 Alarm station location. At least one manual fire alarm and emergency system shutdown station shall be readily accessible to operating personnel. Where access to this station is likely to involve exposure to danger, an additional station shall be located adjacent to an exit from the area. | (N)2404.8.1.2 Alarm station location. (Section deleted) |  | use 2012 language | delete? see above for access
2404.8.2 Ventilation interlock prohibited. Air makeup and flammable vapor area exhaust systems shall not be interlocked with the fire alarm system and shall remain in operation during a fire alarm condition. Exception: Where the type of fire-extinguishing system used requires such ventilation to be discontinued, air makeup and exhaust systems shall shut down and dampers shall close. | (N)2404.8.2 Ventilation interlock prohibited. (Section deleted) |  | use 2012 language | 2404.8.2 Ventilation interlock prohibited. Unless otherwise permitted by the applicable building code, air makeup and flammable vapor area exhaust systems shall not be interlocked with the fire alarm system and shall remain in operation during a fire alarm condition. Exception: Where perrmited by the applicable buidling code such as where the type of fire-extinguishing system used requires such ventilation to be discontinued and dampers close.
2404.9.3 Ventilation. Positive mechanical ventilation providing a minimum of six complete air changes per hour shall be installed. Such system shall meet the requirements of this code for handling flammable vapor areas. Explosion venting is not required. | (N)2404.9.3 Ventilation. Positive mechanical ventilation providing a minimum of six complete air changes per hour shall be maintained in accordance with the applicable building code. |  |  | no change
2404.9.4 Electrical wiring. Electrical wiring within 10 feet (3048 mm) of the floor and 20 feet (6096 mm) horizontally of the limited spraying space shall be designed for Class I, Division 2 locations in accordance with NFPA 70. | (N)2404.9.4 Electrical wiring. Electrical wiring within 10 feet (3048 mm) of the floor and 20 feet (6096 mm) horizontally of the limited spraying space shall be designed for Class I, Division 2 locations in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | no change |  | 2404.9.4 Electrical wiring. Electrical wiring within 10 feet (3048 mm) of the floor and 20 feet (6096 mm) horizontally of the limited spraying space shall be maintained as required for hazardous location in accordance with NFPA 70 and Chapter 6.
2405.2 Location of dip-tank operations. Dip-tank operations conducted in buildings used for Group A, I or R occupancies shall be located in a room designed for that purpose, equipped with an approved automatic sprinkler system and separated vertically and horizontally from other areas in accordance with the International Building Code. | (N)2405.2 Location of dip-tank operations. (Section deleted) |  | use 2012 language | 2405.2 Location of dip-tank operations. Dip-tank operations conducted in buildings used for Group A, I or R occupancies shall be located in a room designed for that purpose, equipped with an approved automatic sprinkler system and separated vertically and horizontally from other areas in accordance with the applicable building code.
2405.3 Construction of dip tanks. Dip tanks shall be constructed in accordance with Sections 2405.3.1 through 2405.3.4.3 and NFPA 34. Dip tanks, including drain boards, shall be constructed of noncombustible material and their supports shall be of heavy metal, reinforced concrete or masonry. | (N)2405.3 Construction of dip tanks. (Section deleted) |  | use 2012 language. this is not building construction related. it deals with what the tank is made of | 2405.3 Construction of dip tanks. Unless regulated by the applicable building code, dip tanks shall be constructed in accordance with Sections 2405.3.1 through 2405.3.4.3 and NFPA 34. Dip tanks, including drain boards, shall be constructed of noncombustible material and their supports shall be of heavy metal, reinforced concrete or masonry.
2405.3.1 Overflow. Dip tanks greater than 150 gallons (568 L) in capacity or 10 square feet (0.93 m2) in liquid surface area shall be equipped with a trapped overflow pipe leading to an approved location outside the building. The bottom of the overflow connection shall not be less than 6 inches (152 mm) below the top of the tank. | (N)2405.3.1 Overflow. Overflow piping required for dip tanks shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2405.3.1 Overflow. To operate dip tanks greater than 150 gallons (568 L) in capacity or 10 square feet (0.93 m2) in liquid surface area, they shall be equipped with a trapped overflow pipe leading to an approved location outside the building. The bottom of the overflow connection shall not be less than 6 inches (152 mm) below the top of the tank.
2405.3.2 Bottom drains. Dip tanks greater than 500 gallons (1893 L) in liquid capacity shall be equipped with bottom drains that are arranged to automatically and manually drain the tank quickly in the event of a fire unless the viscosity of the liquid at normal atmospheric temperature makes this impractical. Manual operation shall be from a safe, accessible location. Where gravity flow is not practicable, automatic pumps shall be provided. Such drains shall be trapped and discharged to a closed, vented salvage tank or to an approved outside location. Exception: Dip tanks containing Class IIIB combustible liquids where the liquids are not heated above room temperature and the process area is protected by automatic sprinklers. | (N)2405.3.2 Bottom drains. Bottom drains required for dip tanks shall be maintained in accordance with the applicable building code. Manual operation shall be from a safe, accessible location. Where gravity flow is not practicable, automatic pumps shall be provided. |  | add "and the International Fire Code" because the building code does not address this | 2405.3.2 Bottom drains. Dip tanks greater than 500 gallons (1893 L) in liquid capacity shall only be operated with bottom drains that are arranged to automatically and manually drain the tank quickly in the event of a fire unless the viscosity of the liquid at normal atmospheric temperature makes this impractical. Manual operation shall be from a safe, accessible location. Where gravity flow is not practicable, automatic pumps shall be provided. Such drains shall be trapped and discharged to a closed, vented salvage tank or to an approved outside location. Exception: Dip tanks containing Class IIIB combustible liquids where the liquids are not heated above room temperature and the process area is protected by automatic sprinklers.
2405.4 Fire protection. Dip-tank operations shall be protected in accordance with Sections 2405.4.1 through 2405.4.2. | (N)2405.4 Fire protection. Dip tank operations shall be protected in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | (N)2405.4 Fire protection. Dip tank operations shall be protected with a fire protection system in accordance with the applicable building code and maintained in accordance with Chapter 9.
2405.4.1 Fixed fire-extinguishing equipment. An approved automatic fire-extinguishing system or dip-tank cover in accordance with Section 2405.3.4 shall be provided for the following dip tanks: 1.Dip tanks less than 150 gallons (568 L) in capacity or 10 square feet (0.93 m2) in liquid surface area. 2.Dip tanks containing a liquid with a flash point below 110°F (43°C) used in such manner that the liquid temperature could equal or be greater than its flash point from artificial or natural causes, and having both a capacity of more than 10 gallons (37.9 L) and a liquid surface area of more than 4 square feet (0.37 m2). | (N)2405.4.1 Fixed fire-extinguishing equipment. Fixed fire-extinguishing equipment required for dip tanks shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2405.4.1 Fixed fire-extinguishing equipment. Unless otherwise permitted by the applicable building code, an approved automatic fire-extinguishing system or dip-tank cover in accordance with Section 2405.3.4 shall be provided for the following dip tanks: 1.Dip tanks less than 150 gallons (568 L) in capacity or 10 square feet (0.93 m2) in liquid surface area. 2.Dip tanks containing a liquid with a flash point below 110°F (43°C) used in such manner that the liquid temperature could equal or be greater than its flash point from artificial or natural causes, and having both a capacity of more than 10 gallons (37.9 L) and a liquid surface area of more than 4 square feet (0.37 m2)
2405.4.1.1 Fire-extinguishing system. An approved automatic fire-extinguishing system shall be provided for dip tanks with a 150-gallon (568 L) or more capacity or 10 square feet (0.93 m2) or larger in a liquid surface area. Fire-extinguishing system design shall be in accordance with NFPA 34. | (N)2405.4.1.1 Fire-extinguishing system. Fire-extinguishing systems provided for dip tanks maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2405.4.1.1 Fire-extinguishing system. Unless otherwise permited by the applicable building code, an approved automatic fire-extinguishing system shall be provided for dip tanks with a 150-gallon (568 L) or more capacity or 10 square feet (0.93 m2) or larger in a liquid surface area. Fire-extinguishing system design shall be in accordance with NFPA 34.
2405.7 Ventilation of flammable vapor areas. Flammable vapor areas shall be provided with mechanical ventilation adequate to prevent the dangerous accumulation of vapors. Required ventilation systems shall be arranged such that the failure of any ventilating fan shall automatically stop the dipping conveyor system. | (N)2405.7 Ventilation of flammable vapor areas. Ventilation provided for flammable vapor areas shall be maintained in accordance with the applicable building code. |  | use 2012 language- this is operational not construction related | 2405.7 Ventilation of flammable vapor areas. Flammable vapor areas shall be operated with mechanical ventilation adequate to prevent the dangerous accumulation of vapors in accordance with the applicable building code. Where required, ventilation systems shall be maintained such that the failure of any ventilating fan shall automatically stop the dipping conveyor system.
2405.9.1 Location. Tanks shall be located as far as practical from furnaces and shall not be located on or near combustible floors. | (N)2405.9.1 Location. (Section deleted) |  | use 2012 language. this is not building construction related. its operational and deals with what the floor is made of | 2405.9.1 Location. Unless otherwise required by the applicable building code, tanks shall be located as far as practical from furnaces and shall not be located on or near combustible floors.
2405.9.2 Hoods. Tanks shall be provided with a noncombustible hood and vent or other approved venting means, terminating outside of the structure to serve as a vent in case of a fire. Such vent ducts shall be treated as flues and proper clearances shall be maintained from combustible materials. | (N)2405.9.2 Hoods. Hoods provided for tanks shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2405.9.2 Hoods. Unless otherwise reuired by the applicable building code, tanks shall be operated only with a noncombustible hood and vent or other approved venting means, terminating outside of the structure to serve as a vent in case of a fire. Such vent ducts shall be treated as flues and proper clearances shall be maintained from combustible materials.
2405.9.3 Alarms. Tanks shall be equipped with a high-temperature limit switch arranged to sound an alarm when the temperature of the quenching medium reaches 50°F (10°C) below the flash point. | (N)2405.9.3 Alarms. (Section deleted) |  | use 2012 language. this is an operational issue not building construction | 2405.9.3 Alarms. Tanks shall be operated with a high-temperature limit switch maintained to sound an alarm when the temperature of the quenching medium reaches 50°F (10°C) below the flash point or other approved level as required by the applicable building code.
2405.9.4 Fire protection. Hardening and tempering tanks greater than 500 gallons (1893 L) in capacity or 25 square feet (2.3 m2) in liquid surface area shall be protected by an approved automatic fire-extinguishing system complying with Chapter 9. | (N)2405.9.4 Fire protection. Fire protection provided hardening and tempering tanks shall be maintained in accordance with the applicable building code. |  | use 2012 language. this is an operational issue not building construction | 2405.9.4 Fire protection. Unless otherwise required by the applicable building code, hardening and tempering tanks greater than 500 gallons (1893 L) in capacity or 25 square feet (2.3 m2) in liquid surface area shall be protected by an approved automatic fire-extinguishing system maintained in accordance with Chapter 9.
2405.10.1 Paint supply. Paint shall be supplied by a gravity tank not exceeding 10 gallons (38 L) in capacity or by direct low-pressure pumps arranged to shut down automatically in case of a fire by means of approved heat-actuated devices. | (N)2405.10.1 Paint supply. (Section deleted) |  | use 2012 language. this is an operational issue not building construction | 2405.10.1 Paint supply. Unless otherwise requried by the applicable building code, paint operations shall be supplied by a gravity tank not exceeding 10 gallons (38 L) in capacity or by direct low-pressure pumps arranged to shut down automatically in case of a fire by means of approved heat-actuated devices.
2405.11 Roll-coating operations. Roll-coating operations shall comply with Section 2405.10. In roll-coating operations utilizing flammable or combustible liquids, sparks from static electricity shall be prevented by electrically bonding and grounding all metallic rotating and other parts of machinery and equipment and by the installation of static collectors, or by maintaining a conductive atmosphere such as a high relative humidity. | (N)2405.11 Roll-coating operations. Rollcoating operations shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2405.11 Roll-coating operations. Roll-coating operations shall comply with Section 2405.10. In roll-coating operations utilizing flammable or combustible liquids, sparks from static electricity shall be prevented by electrically bonding and grounding all metallic rotating and other parts of machinery and equipment and by the installation of static collectors, or by maintaining a conductive atmosphere such as a high relative humidity.
2406.2 Location. Powder coating operations shall be conducted in enclosed powder coating rooms, enclosed powder coating facilities which are ventilated or ventilated spray booths. | (N)2406.2 Location. Powder coating operations shall be conducted in enclosed powder coating rooms, enclosed powder coating facilities that are ventilated, or ventilated spray booths and in accordance with applicable building code. |  | add "and the International Fire Code" because the building code does not address this | no change
2406.3 Construction of powder coating rooms and booths. Powder coating rooms shall be constructed of noncombustible materials. Spray booths shall be constructed in accordance with Section 2404.3.2. Exception: Listed spray-booth assemblies that are constructed of other materials shall be allowed. | (N)2406.3 Construction of powder coating room and booths. (Section deleted) |  | use 2012 language- not building construction related. it only addresses what the room is made of | 2406.3 Construction of powder coating rooms and booths. Powder coating rooms shall be constructed of noncombustible materials in accordance with the appliable building code. Spray booths shall be constructed in accordance with Section 2404.3.2. Exception: Listed spray-booth assemblies that are constructed of other materials shall be allowed. |  | 2406.3 Construction of powder coating rooms and booths. Powder coating rooms shall be constructed in accordance with the applicable building code.
2406.4 Fire protection. Areas used for powder coating shall be protected by an approved automatic fire-extinguishing system complying with Chapter 9. | (N)2406.4 Fire protection. Fireextinguishing systems provided for areas used for powder coating shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2406.4 Fire protection. Areas used for powder coating shall be protected by an approved automatic fire-extinguishing system maintained in accordance with Chapter 9.
2406.4.1 Additional protection for fixed systems. Automated powder application equipment shall be protected by the installation of an approved, supervised flame detection apparatus that shall react to the presence of flame within 0.5 second and shall accomplish all of the following: 1.Shutting down of energy supplies (electrical and compressed air) to conveyor, ventilation, application, transfer and powder collection equipment. 2.Closing of segregation dampers in associated ductwork to interrupt airflow from application equipment to powder collectors. 3.Activation of an alarm that is audible throughout the powder coating room or booth. | (N)2406.4.1 Additional protection for fixed systems. (Section deleted) |  |  | no change
2406.6.4 Grounding and bonding. Precautions shall be taken to minimize the possibility of ignition by static electrical sparks through static bonding and grounding, where possible, of powder transport, application and recovery equipment. | (N)2406.6.4 Grounding and bonding. Grounding and bonding provided for powder coating operations shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2406.6.4 Grounding and bonding. Precautions shall be taken to minimize the possibility of ignition by static electrical sparks through static bonding and grounding, where possible, of powder transport, application and recovery equipment.
2406.7 Ventilation. Exhaust ventilation shall be sufficient to maintain the atmosphere below one-half the minimum explosive concentration for the material being applied. Nondeposited, air-suspended powders shall be removed through exhaust ducts to the powder recovery system. | (N)2406.7 Ventilation. Exhaust ventilation shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2406.7 Ventilation. Exhaust ventilation shall be sufficient to maintain the atmosphere below one-half the minimum explosive concentration for the material being applied. Nondeposited, air-suspended powders shall be removed through exhaust ducts to the powder recovery system.
2407.2 Location and clear space. A space of at least twice the sparking distance shall be maintained between goods being painted or deteared and electrodes, electrostatic atomizing heads or conductors. A sign stating the sparking distance shall be conspicuously posted near the assembly. Exception: Portable electrostatic paint-spraying apparatus listed for use in Class I, Division 1, locations. | (N)2407.2 Location and clear space. A sign stating the sparking distance shall be conspicuously posted near the assembly. The location and clear space required for electrostatic apparatus and devices shall be maintained in accordance with the applicable building code and manufacturer's instructions. |  | add "and the International Fire Code" because the building code does not address this | 2407.2 Location and clear space. A space of at least twice the sparking distance shall be maintained between goods being painted or deteared and electrodes, electrostatic atomizing heads or conductors. A sign stating the sparking distance shall be conspicuously posted near the assembly. Exception: Portable electrostatic paint-spraying apparatus listed for use in Class I, Division 1, locations.
2407.3 Construction of equipment. Electrodes and electrostatic atomizing heads shall be of approved construction, rigidly supported in permanent locations and effectively insulated from ground. Insulators shall be nonporous and noncombustible. Exception: Portable electrostatic paint-spraying apparatus listed for use in Class I, Division 1, locations. | (N)2407.3 Construction equipment. (Section deleted) |  | use 2012 language. this is not building construction related | 2407.3 Construction of equipment. Electrodes and electrostatic atomizing heads shall be maintained of approved construction, rigidly supported in permanent locations and effectively insulated from ground. Insulators shall be nonporous and noncombustible. Exception: Portable electrostatic paint-spraying apparatus listed for use in Class I, Division 1, locations.
2407.3.1 Barriers. Booths, fencing, railings or guards shall be placed about the equipment such that either by their location or character, or both, isolation of the process is maintained from plant storage and personnel. Railings, fencing and guards shall be of conductive material, adequately grounded, and at least 5 feet (1524 mm) from processing equipment. Exception: Portable electrostatic paint-spraying apparatus listed for use in Class I, Division 1, locations. | (N)2407.3.1 Barriers. Booths, fencing, railings or guards shall be in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2407.3.1 Barriers. Booths, fencing, railings or guards shall be maintained about the equipment such that either by their location or character, or both, isolation of the process is maintained from plant storage and personnel. Railings, fencing and guards shall be of conductive material, adequately grounded, and at least 5 feet (1524 mm) from processing equipment. Exception: Portable electrostatic paint-spraying apparatus listed for use in Class I, Division 1, locations.
2407.4 Fire protection. Areas used for electrostatic spray finishing with fixed equipment shall be protected with an approved automatic fire-extinguishing system complying with Chapter 9 and Section 2407.4.1. | (N)2407.4 Fire protection. Fireextinguishing systems provided for areas used for electrostatic spray finishing with fixed equipment shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2407.4 Fire protection. Areas used for electrostatic spray finishing with fixed equipment shall be protected with an approved automatic fire-extinguishing system and maintained in accordance with Chapter 9.
2407.4.1 Protection for automated liquid electrostatic spray application equipment. Automated liquid electrostatic spray application equipment shall be protected by the installation of an approved, supervised flame detection apparatus that shall, in the event of ignition, react to the presence of flame within 0.5 second and shall accomplish all of the following: 1.Activation of a local alarm in the vicinity of the spraying operation and activation of the building alarm system, if such a system is provided. 2.Shutting down of the coating material delivery system. 3.Termination of all spray application operations. 4.Stopping of conveyors into and out of the flammable vapor areas. 5.Disconnection of power to the high-voltage elements in the flammable vapor areas and disconnection of power to the system. | (N)2407.4.1 Protection for automated liquid electrostatic spray application equipment. Flame detection apparatus required for automated liquid electrostatic spray application equipment shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2407.4.1 Protection for automated liquid electrostatic spray application equipment. Where provided, automated liquid electrostatic spray application equipment shall maintain an approved, supervised flame detection apparatus that shall, in the event of ignition, react to the presence of flame within 0.5 second and shall accomplish all of the following: 1.Activation of a local alarm in the vicinity of the spraying operation and activation of the building alarm system, if such a system is provided. 2.Shutting down of the coating material delivery system. 3.Termination of all spray application operations. 4.Stopping of conveyors into and out of the flammable vapor areas. 5.Disconnection of power to the high-voltage elements in the flammable vapor areas and disconnection of power to the system.
2407.7 Ventilation. The flammable vapor area shall be ventilated in accordance with Section 2404.7. | (N)2407.7 Ventilation. Ventilation provided for flammable vapor areas shall be maintained in accordance with the applicable building code. |  |  | no change
2407.8 Emergency shutdown. Electrostatic apparatus shall be equipped with automatic controls operating without time delay to disconnect the power supply to the high-voltage transformer and signal the operator under any of the following conditions: 1.Stoppage of ventilating fans or failure of ventilating equipment from any cause. 2.Stoppage of the conveyor carrying articles past the high-voltage grid. 3.Occurrence of a ground or an imminent ground at any point of the high-voltage system. 4.Reduction of clearance below that required in Section 2407.2. | (N)2407.8 Emergency shutdown. Emergency shutdown controls shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2407.8 Emergency shutdown. Where provided, electrostatic apparatus shall be maintained with automatic controls operating without time delay to disconnect the power supply to the high-voltage transformer and signal the operator under any of the following conditions: 1.Stoppage of ventilating fans or failure of ventilating equipment from any cause. 2.Stoppage of the conveyor carrying articles past the high-voltage grid. 3.Occurrence of a ground or an imminent ground at any point of the high-voltage system. 4.Reduction of clearance below that required in Section 2407.2.
2407.9 Ventilation interlock. Hand electrostatic equipment shall be interlocked with the ventilation system for the spraying area so that the equipment cannot be operated unless the ventilating system is in operation. | (N)2407.9 Ventilation interlock. Ventilation interlock required for electrostatic equipment shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2407.9 Ventilation interlock. Unless otherwise permitted by the applicable building code, hand electrostatic equipment shall be interlocked with the ventilation system for the spraying area so that the equipment cannot be operated unless the ventilating system is in operation.
2408.2 Use of organic peroxide coatings.Spraying operations involving the use of organic peroxides and other dual-component coatings shall be conducted in approved sprinklered spray booths complying with Section 2404.3.2. | (N)Use of organic peroxide coatings. (Section deleted) |  | use 2012 language and add "in accordance with the USBC" | 2408.2 Use of organic peroxide coatings.Spraying operations involving the use of organic peroxides and other dual-component coatings shall be conducted in approved sprinklered spray booths complying with the applicable building code.
2409.3 Fire protection. Resin application areas shall be protected by an automatic sprinkler system. The sprinkler system design shall not be less than that required for Ordinary Hazard, Group 2, with a minimum design area of 3,000 square feet (279 m2). Where the materials or storage arrangements are required by other regulations to be provided with a higher level of sprinkler system protection, the higher level of sprinkler system protection shall be provided. | (N)2409.3 Fire protection. Automatic sprinkler systems provided for resin application areas shall be maintained in accordance with the applicable building code. |  | add "and the International Fire Code" because the building code does not address this | 2409.3 Fire protection. Unless otherwise permitted by the applicable building code, resin application areas shall be protected by an automatic sprinkler system.
409.6 Ventilation. Mechanical ventilation shall be provided throughout resin application areas in accordance with Section 2404.7. The ventilation rate shall be adequate to maintain the concentration of flammable vapors in the resin application area at or below 25 percent of the LFL. Exception: Mechanical ventilation is not required for buildings that have 75 percent of the perimeter unenclosed. | (N)2409.6 Ventilation. Mechanical ventilation shall be maintained in accordance with the applicable building code. |  | no change? | 409.6 Ventilation. Mechanical ventilation shall be maintained throughout resin application areas unless othewise permitted by the applicable building code. The ventilation rate shall be adequate to maintain the concentration of flammable vapors in the resin application area at or below 25 percent of the LFL. Exception: Mechanical ventilation is not required for buildings that have 75 percent of the perimeter unenclosed.
2409.6.1 Local ventilation. Local ventilation shall be provided inside of workpieces where personnel will be under or inside of the workpiece. | (N)2409.6.1 Local ventilation. Local ventilation shall be maintained in accordance with the applicable building code. |  | no change? | 2409.6.1 Local ventilation. Local ventilation shall be provided inside of workpieces where personnel will be under or inside of the workpiece.

## Ch25 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
2501.2 Permits. Permits shall be required as set forth in Section 107.2. | 2501.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | No change.
2501.3 Ethylene generators. Approved ethylene generators shall be operated and maintained in accordance with Section 2506. | 2501.3 Ethylene generators. Approved ethylene generators shall be operated and maintained in accordance with the applicable building code. |  |  | 2501.3 Ethylene generators. Approved ethylene generators shall be operated and maintained in accordance with Section 2506. |  | Chapter 25 recognizes the use of listed ethylene generators as a means of safely producing ethylene concentrations needed to ripen crops. This section requires that those devices be properly operated and maintained
2503.2 Dispensing. Valves controlling discharge of ethylene shall provide positive and fail-closed control of flow and shall be set to limit the concentration of gas in air below 1,000 parts per million (ppm). | (N)2503.2 Dispensing. Valves controlling discharge of ethylene shall be maintained in accordance with the applicable building code. |  | Design/ construction related? | 2503.2 Dispensing. Valves controlling discharge of ethylene shall be maintained to limit the concentration of gas in accordance with this chapter and the applicable building code. |  | Although the hazards of using ethylene should be of considerable concern, technological innovation has produced a safe alternative to the old method of distributing ethylene to the ripening rooms. In the past, compressed ethylene gas in cylinders was piped through regulating equipment into rooms. Regulating equipment was calibrated to restrict gas quantity to a volume that would produce concentrations below the lower explosive gas limit; however, excessive concentrations occasionally escaped and uncontrolled ignition sources produced serious explosions. Ideally, gas sensors should be used to stop gas flow as it approaches the desired level. Manual overrides must be provided to interrupt the gas flow if a danger exists. A 1:1,000 concentration is only 0.1 percent in air. The LFL of ethylene is 2.6 percent. When used properly, this gas poses little hazard.
2504.1 Ignition prevention. Sources of ignition shall be controlled or protected in accordance with this section and Chapter 3. | (N)2504.1 Ignition prevention. Sources of ignition shall be controlled or protected in accordance with the applicable building code. |  | Not construction related | 2504.1 Ignition prevention. Sources of ignition shall be controlled or protected in accordance with this section and Chapter 3. |  | There are no ignition prevention requirements in the building code. Lighted smoking materials and other open-flame sources are prohibited in crop-ripening and color-processing rooms. This prohibition should also be extended to the immediate vicinity of the entrance to such rooms. “No Smoking” signs are to be conspicuously posted and stringently enforced.
2504.2 Electrical wiring and equipment. Electrical wiring and equipment, including luminaires, shall be approved for use in Class I, Division 2, Group C hazardous (classified) locations. | (N)2504.2 Electrical wiring and equipment. Electrical wiring and equipment, including luminaires, shall be maintained in accordance with the applicable building code. |  | Design/ construction related? | (N)2504.2 Electrical wiring and equipment. Electrical wiring and equipment, including luminaires, shall be classified and maintained in accordance with Chapter 6, NFPA 70 and remain in accordance with the applicable building code. |  | Maintenance and operation of electrical equipment in flammable vapor areas, not installation. Atmospheres containing ethylene are classified as Class 1, Division 1, Group C hazardous locations by NFPA 70. All electrical wiring and equipment must be suitably listed and labeled for use in such atmospheres.
2504.3 Static electricity. Containers, piping and equipment used to dispense ethylene shall be bonded and grounded to prevent the discharge of static sparks or arcs. | (N)2504.3 Static electricity. Bonding and grounding provided for containers, piping and equipment shall be maintained in accordance with the applicable building code. |  |  | 2504.3 Static electricity. Bonding and grounding provided for permanent containers, piping and equipment shall be maintained in accordance with the applicable building code. Portable containers, piping and equipment shall be bonded and grounded in accordance with Chapter 57. |  | Bonding and grounding is an operational issue, not construction. Suitable grounds must be provided on all ethylene-handling systems and equipment to permit the dissipation of static electricity, thus preventing the generation of static sparks. Electrically isolated sections of systems and equipment must be independently grounded. NFPA 77 provides valuable guidance on this topic. Grounding and bonding should be in accordance with NFPA 70
2504.5 Heating.Heating shall be by indirect means utilizing low-pressure steam, hot water or warm air. Exception: Electric or fuel-fired heaters approved for use in hazardous (classified) locations which are installed and operated in accordance with the applicable provisions of NFPA 70, the International Mechanical Code or the International Fuel Gas Code. | (N)2504.5 Heating. Heating shall be maintained in accordance with the applicable building code. |  |  | 2504.5 Heating. Heating shall be maintained in accordance with chapter 6 and the applicable building code. |  | There are no heating device maintenance requirements in the building code. Wherever practical, heat for crop-ripening and coloring rooms should be indirect (steam, hot water or warm air) to eliminate sparks or open-flame ignition hazards.
2506.1 Ethylene generators.Ethylene generators shall be listed and labeled by an approved testing laboratory, approved by the fire code official and used only in approved rooms in accordance with the ethylene generator manufacturer’s instructions. The listing evaluation shall include documentation that the concentration of ethylene gas does not exceed 25 percent of the lower explosive limit (LEL). | (N)2506.1 Ethylene generators. Ethylene generators shall be listed and labeled by an approved testing laboratory, approved, and used only in approved rooms in accordance with the ethylene generator manufacturer's instructions. The listing evaluation shall include documentation that the concentration of ethylene gas does not exceed 25% of the lower explosive limit (LEL). |  | Issue with who approves the generator. Many of these are portable and may not require a building permit to install. The fire official can have a permit to control location. | No change.
2506.2 Ethylene generator rooms. Ethylene generators shall be used in rooms having a volume of not less than 1,000 cubic feet (28 m3). Rooms shall have air circulation to ensure even distribution of ethylene gas and shall be free from sparks, open flames or other ignition sources | (N)2506.2 Ethylene generator rooms. Ethylene generator rooms shall be maintained in accordance with the applicable building code. |  | Issue with where a portable generator could be used. Many of these are portable and may not require a building permit to install. | 2506.2 Ethylene generator rooms. Portable ethylene generators shall be used in rooms having a volume of not less than 1,000 cubic feet (28 m3). Rooms shall have air circulation to ensure even distribution of ethylene gas and shall be free from sparks, open flames or other ignition sources. |  | There are no operations or maintenance requirements for portable ethylene generators in the building code. Because ethylene generators are portable, the level of hazard associated with their use in closed rooms can change each time one is moved to a new ripening room. The intent of this section is to reduce the hazard potential by requiring that ethylene generators be used only in ripening rooms having a minimum volume of 1,000 cubic feet (28 m3) [10 feet by 10 feet by 10 feet (3048 mm by 3048 mm by 3048 mm)], that are free from ignition hazards and have air circulation to distribute the ethylene gas evenly throughout the space to avoid the potential for pockets of gas having concentrations approaching or exceeding 25 percent of the LEL.
DRAFT - 4.11.2019

## Ch26 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
2601.2 Permits. Permits shall be required as set forth in Section 107.2. | 2601.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change

## Ch27 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
2701.1 Scope. Semiconductor fabrication facilities and comparable research and development areas classified as Group H-5 shall comply with this chapter and the International Building Code. The use, storage and handling of hazardous materials in Group H-5 shall comply with this chapter, other applicable provisions of this code and the International Building Code. | 2701.1 Scope. Semiconductor fabrication facilities and comparable research and development areas classified as Group H-5 shall comply with this chapter to the extent that the provisions of this chapter relate to operation and maintenance and not to the construction of Group H-5 buildings or structures. |  |  | 2701.1 Scope. The operation and maintenance of semiconductor fabrication and comparable research and development areas classified as Group H-5 shall comply with this chapter. The use, storage and handling of hazardous materials in Group H-5 shall comply with this chapter, other applicable provisions of this code and requirements of the applicable building code.
2701.4 Existing buildings and existing fabrication areas. Existing buildings and existing fabrication areas shall comply with this chapter, except that transportation and handling of HPM in corridors and enclosures for stairways and ramps shall be allowed when in compliance with Section 2705.3.2 and the International Building Code. | (N)2701.4 Existing buildings and existing fabrication areas. (Section deleted) |  |  | 2701.4 Existing buildings and existing fabrication areas. Operations in existing buildings and existing fabrication areas shall comply with this chapter, except that transportation and handling of HPM in corridors and enclosures for stairways and ramps shall bea llowed when in compliance with Section 2705.3.2 and requirements of the applicable building code.
2701.5 Permits. Permits shall be required as set forth in Section 107.2. | 2701.5 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
2703.1.3 Signals. The emergency control station shall receive signals from emergency equipment and alarm and detection systems. Such emergency equipment and alarm and detection systems shall include, but not be limited to, the following where such equipment or systems are required to be provided either in this chapter or elsewhere in this code: 1.Automatic sprinkler system alarm and monitoring systems. 2.Manual fire alarm systems. 3.Emergency alarm systems. 4.Continuous gas detection systems. 5.Smoke detection systems. 6.Emergency power system. 7.Automatic detection and alarm systems for pyrophoric liquids and Class 3 water-reactive liquids required by Section 2705.2.3.4. 8.Exhaust ventilation flow alarm devices for pyrophoric liquids and Class 3 water-reactive liquids cabinet exhaust ventilation systems required by Section 2705.2.3.4. | (N)2703.1.3 Signals. Emergency equipment and alarm and detection systems providing signals to emergency control stations shall be maintained in accordance with the applicable building code. |  | Requirements for Semiconductor Fabrication Facilities first appeared in the 1987 BOCA Fire Prevention Code. An Emergency Control Station was defined as "An approved location on the premises of an HPM use facility, where signals for emergency equipment are recieved. Gas detection systems were specificially required to be connected to the emergency control station. The 2000 IBC required systems 1 through 6 to send signals to the Emergency Control Station. The requirements for systems 7 and 8 dealing with pyrophoric and water-reactive liquids first appeared in the 2006 Fire Code. | 2703.1.3 Signals. Unless specifically approved otherwise in accordance with the applicable building code, the emergency control station shall recived signals from emergency equipment and alarm and detection systems. Such emergency equipment and alarm and detections systems shall include, but not be limited to, the following where such equipment or systems are required to be provided by the applicable building code. 1. Automatic sprinkler system alarm and monitoring systems. 2. Manual fire alarm systems. 3. Emergency alarm systems. 4. Continuous gas detection systems. 5. Smoke detection systems. 6. Emergency power system. 7. Automatic detection and alarm systems for pyrophoric liquids and Class 3 water-reactive liquids required by Section 2705.2.3.4. 8. Exhaust ventilation flow alarm devices for pyrophoric liquids and Class 3 water-reactive liquids cabinet exhaust ventilation sysetms required by Section 2704.2.3.4.
2703.2.2 General requirements. In addition to the requirements in Section 2703.2, systems, equipment and processes shall also comply with Section 5003.2, other applicable provisions of this code, the International Building Code and the International Mechanical Code. | 2703.2.2 General requirements. In addition to the requirements in Section 2703.2, systems, equipment and processes shall also comply with Section 5003.2, other applicable provisions of this code. |  |  | 2703.2.2 General requirements. In addition to the requriements in Section 2703.2, systems, equipment and other processes shall also comply with Section 5003.2, other applicable provisions of this code and the applicable building code.
2703.3 Construction requirements. Construction of semiconductor fabrication facilities shall be in accordance with Sections 2703.3.1 through 2703.3.9. | (N)2703.3 Construction requirements. (Section deleted)
2703.3.1 Fabrication areas. Construction and location of fabrication areas shall comply with the International Building Code. | (N)2703.3.1 Fabrication areas. (Section deleted) |  |  | no change
2703.3.2 Pass-throughs in exit access corridors. Pass-throughs in exit access corridors shall be constructed in accordance with the International Building Code. | (N)2703.3.2 Pass-throughs in exit access corridors. Pass-throughs in exit access corridors shall be in accordance with the applicable building code. |  |  | 2703.3.2 Pass-throughs in exit access corridors. Pass-throughs in exit access corridors shall comply with the applicable building code.
2703.3.3 Liquid storage rooms. Liquid storage rooms shall comply with Chapter 57 and the International Building Code. | (N)2703.3.3 Liquid storage rooms. Liquid storage rooms shall be maintained in accordance with the applicable building code. |  |  | 2703.3.3 Liquid storage rooms. Liquid storage rooms shall comply with Chapter 57 and the applicable building code.
2703.3.4 HPM rooms. HPM rooms shall comply with the International Building Code. | (N)2703.3.4 HPM rooms. Hazardous production materials (HPM) rooms shall be maintained in accordance with the applicable building code. |  |  | 2703.3.4 HPM rooms. HPM rooms shall comply with the applicable building code.
2703.3.5 Gas cabinets. Gas cabinets shall comply with Section 5003.8.6. | (N)2703.3.5 Gas cabinets. Gas cabinets shall be maintained in accordance with the applicable building code |  |  | 2703.3.5 Gas cabinets. Gas cabinets shall comply with Section 5003.8.6.
2703.3.6 Exhausted enclosures. Exhausted enclosures shall comply with Section 5003.8.5. | (N)2703.3.6 Exhausted enclosures. Exhausted enclosures shall be maintained in accordance with the applicable building code. |  |  | 2703.3.6 Exhausted enclosures. Exhausted enclosures shall be maintained in accordance with Section 5003.8.5 and remain in accordance with the applicable building code.
2703.3.7 Gas rooms. Gas rooms shall comply with Section 5003.8.4. | (N)2703.3.7 Gas rooms. Gas rooms shall be maintained in accordance with the applicable building code |  |  | 2703.3.7 Gas rooms. Gas rooms shall be maintained in accordance with Section 5003.8.4 and remain in accordance with the applicable building code.
2703.3.8 Service corridors. Service corridors shall comply with Section 2705.3 and the International Building Code. | (N)2703.3.8 Service corridors. Service corridors shall be maintained in accordance with the applicable building code. |  |  | 2703.3.8 Service corridors. Service corridors shall compy with Section 2705.3 and the remain in accordance with the applicable building code.
2703.7 Electrical wiring and equipment. Electrical wiring and equipment in HPM facilities shall comply with Sections 2703.7.1 through 2703.7.3. | (N)2703.7 Electrical wiring and equipment. Electrical wiring and equipment in HPM facilities shall be maintained in accordance with the applicable building code. |  |  | 2703.7 Electrical wiring and equipment. Electrical wiring and equipment in HPM facilities shall comply with Sections 2703.7.1 through 2703.7.3.
2703.7.1 Fabrication areas. Electrical wiring and equipment in fabrication areas shall comply with NFPA 70. | (N)2703.7.1 Fabrication areas. Electrical wiring and equipment in fabrication areas shall be maintained in accordance with the applicable building code. |  |  | 2703.7.1 Fabrication areas. Electrical wiring and equipment in fabrication areas shall be maintained in accordance with NFPA 70 and remain in accordance with the applicable building code.
2703.7.2 Workstations. Electrical equipment and devices within 5 feet (1524 mm) of workstations in which flammable or pyrophoric gases or flammable liquids are used shall comply with NFPA 70 for Class I, Division 2 hazardous locations. Workstations shall not be energized without adequate exhaust ventilation in accordance with Section 2703.14. Exception: Class I, Division 2 hazardous electrical equipment is not required when the air removal from the workstation or dilution will prevent the accumulation of flammable vapors and fumes on a continuous basis. | (N)2703.7.2 Workstations. (Section deleted) |  |  | 2703.7.2 Workstations. Electrical equipment and devices within 5 feet (1524 mm) of workstations in which flammable or pyrophoric gases or flammable liquids are used shall be maintained in accordance with NFPA 70 for hazardous locations. Workstations shall not be energized without adequate exhaust ventilation in accordance with Section 2703.14. Exception: Not required when the air removal from the workstation or dilution will prevent the accumulation of flammable vapors and fumes on a continuous basis.
2703.7.3 Hazardous production material (HPM) rooms, gas rooms and liquid storage rooms. Electrical wiring and equipment in HPM rooms, gas rooms and liquid storage rooms shall comply with NFPA 70. | (N)2703.7.3 HPM rooms, gas rooms, and liquid storage rooms. Electrical wiring and equipment in HPM rooms, gas rooms, and liquid storage rooms shall be maintained in accordance with the applicable building code. |  |  | 2703.7.3 Hazardous production material (HPM) rooms, gas rooms and liquid storage rooms. Electrical wiring and equipment in HPM rooms, gas rooms and liquid storage rooms shall be maintained in accordance with NFPA 70.
2703.10 Automatic sprinkler system. An approved automatic sprinkler system shall be provided in accordance with Sections 2703.10.1 through 2703.10.5 and Chapter 9. | (N)2703.10 Automatic sprinkler system. Automatic sprinkler systems shall be maintained in accordance with the applicable building code. |  |  | 2703.10 Automatic sprinkler system. An approved automatic sprinkler system shall be maintained in accordance with Chapter 9 and remain in accordance with the applicable building code.
2703.10.1 Workstations and tools. The design of the sprinkler system in the area shall take into consideration the spray pattern and the effect on the equipment. | (N)2703.10.1 Workstations and tools. (Section deleted) |  |  | no change
2703.10.1.1 Combustible workstations. A sprinkler head shall be installed within each branch exhaust connection or individual plenums of workstations of combustible construction. The sprinkler head in the exhaust connection or plenum shall be located not more than 2 feet (610 mm) from the point of the duct connection or the connection to the plenum. When necessary to prevent corrosion, the sprinkler head and connecting piping in the duct shall be coated with approved or listed corrosion-resistant materials. The sprinkler head shall be accessible for periodic inspection. Exceptions: 1.Approved alternative automatic fire-extinguishing systems are allowed. Activation of such systems shall deactivate the related processing equipment. 2.Process equipment which operates at temperatures exceeding 932°F (500°C) and is provided with automatic shutdown capabilities for hazardous materials. 3.Exhaust ducts 10 inches (254 mm) or less in diameter from flammable gas storage cabinets that are part of a workstation. 4.Ducts listed or approved for use without internal automatic sprinkler protection. | (N)2703.10.1.1 Combustible workstations. (Section deleted) |  |  | no change
2703.10.2 Gas cabinets and exhausted enclosures. An approved automatic sprinkler system shall be provided in gas cabinets and exhausted enclosures containing HPM compressed gases. Exception: Gas cabinets located in an HPM room other than those cabinets containing pyrophoric gases. | (N)2703.10.2 Gas cabinets and exhausted enclosures. (Section deleted) |  |  | no change
2703.10.3 Pass-throughs in existing exit access corridors. Pass-throughs in existing exit access corridors shall be protected by an approved automatic sprinkler system. | (N)2703.10.3 Pass-throughs in existing exit access corridors. (Section deleted) |  |  | no change
703.10.4 Exhaust ducts for HPM. An approved automatic sprinkler system shall be provided in exhaust ducts conveying gases, vapors, fumes, mists or dusts generated from HPM in accordance with this section and the International Mechanical Code. | (N)2703.10.4 Exhaust ducts for HPM. (Section deleted) |  |  | no change
2703.10.4.1 Metallic and noncombustible nonmetallic exhaust ducts. An approved automatic sprinkler system shall be provided in metallic and noncombustible nonmetallic exhaust ducts when all of the following conditions apply: 1.When the largest cross-sectional diameter is equal to or greater than 10 inches (254 mm). 2.The ducts are within the building. 3.The ducts are conveying flammable gases, vapors or fumes. | (N)2703.10.4.1 Metallic and noncombustible nonmetallic exhaust ducts. (Section deleted) |  |  | no change
2703.10.4.2 Combustible nonmetallic exhaust ducts. An approved automatic sprinkler system shall be provided in combustible nonmetallic exhaust ducts when the largest cross-sectional diameter of the duct is equal to or greater than 10 inches (254 mm). Exceptions: 1.Ducts listed or approved for applications without automatic sprinkler system protection. 2.Ducts not more than 12 feet (3658 mm) in length installed below ceiling level. | (N)2703.10.4.2 Combustible nonmetallic exhaust ducts. (Section deleted) |  |  | no change
2703.10.4.3 Exhaust connections and plenums of combustible workstations. Automatic fire-extinguishing system protection for exhaust connections and plenums of combustible workstations shall comply with Section 2703.10.1.1. | (N)2703.10.4.3 Exhaust connections and plenums of combustible workstations. (Section deleted) |  |  | no change
2703.10.4.4 Exhaust duct sprinkler system requirements. Automatic sprinklers installed in exhaust duct systems shall be hydraulically designed to provide 0.5 gallons per minute (gpm) (1.9 L/min) over an area derived by multiplying the distance between the sprinklers in a horizontal duct by the width of the duct. Minimum discharge shall be 20 gpm (76 L/min) per sprinkler from the five hydraulically most remote sprinklers. | (N)2703.10.4.4 Exhaust duct sprinkler system requirements. (Section deleted) |  |  | no change
2703.10.4.4.1 Sprinkler head locations. Automatic sprinklers shall be installed at 12-foot (3658 mm) intervals in horizontal ducts and at changes in direction. In vertical runs, automatic sprinklers shall be installed at the top and at alternate floor levels. | (N)2703.10.4.4.1 Sprinkler head locations. (Section deleted) |  |  | no change
2703.10.4.4.2 Control valve. A separate indicating control valve shall be provided for sprinklers installed in exhaust ducts. | (N)2703.10.4.4.2 Control valve. Control valves provided for sprinklers installed in exhaust ducts shall be maintained in accordance with the applicable building code |  |  | no change
2703.10.4.4.3 Drainage. Drainage shall be provided to remove sprinkler water discharged in exhaust ducts. | (N)2703.10.4.4.3 Drainage. Drainage provided to remove sprinkler water discharged in exhaust ducts shall be maintained |  |  | no change
2703.10.4.4.4 Corrosive atmospheres. Where corrosive atmospheres exist, exhaust duct sprinklers and pipe fittings shall be manufactured of corrosion-resistant materials or coated with approved materials. | (N)2703.10.4.4.4 Corrosive atmospheres. (Section deleted) |  |  | no change
2703.10.5 Sprinkler alarms and supervision. Automatic sprinkler systems shall be electrically supervised and provided with alarms in accordance with Chapter 9. Automatic sprinkler system alarm and supervisory signals shall be transmitted to the emergency control station. | (N)2703.10.5 Sprinkler alarms and supervision. Automatic sprinkler systems shall be maintained in accordance with applicable building code |  |  | 2703.10.5 Sprinkler alarms and supervision. Automatic sprinkler systems, associated electronic supervision and alarms shall be maintained in accordance with Chapter 9. Where provided, automatic sprinkler system alarm and supervisory signals shall also remain transmitted to the emergency control station in accordance with the applicable building code.
2703.11 Manual fire alarm system. A manual fire alarm system shall be installed throughout buildings containing a Group H-5 occupancy. Activation of the alarm system shall initiate a local alarm and transmit a signal to the emergency control station. Manual fire alarm systems shall be designed and installed in accordance with Section 907. | (N)2703.11 Manual fire alarm system. Manual fire alarm systems shall be maintained in accordance with the applicable building code. |  |  | 2703.11 Manual fire alarm system. Where provided, a manual fire alarm system shall be maintained in accordance with Chapter 9 and remain throughout buildings containing a Group H-5 occupancy in accordance with the applicable building code. Where provided, activation of the alarm system shall also be maintained to transmit a signal to the emergency control station.
2703.12 Emergency alarm system. Emergency alarm systems shall be provided in accordance with Sections 2703.12.1 through 2703.12.3, Section 5004.9 and Section 5005.4.4. The maximum allowable quantity per control area provisions of Section 5004.1 shall not apply to emergency alarm systems required for HPM. | (N)2703.12 Emergency alarm system. Emergency alarm systems shall be maintained in accordance with the applicable building code. |  |  | 2703.12 Emergency alarm system. Emergency alarm systems shall be maintained in accordance with Chapter 9 and remain in accordance with the applicable building code. Where provided, emergency alarm systems shall also remain transmitted to the emergency control station in accordance with the applicable building code.
2703.12.1 Where required. Emergency alarm systems shall be provided in the areas indicated in Sections 2703.12.1.1 through 2703.12.1.3. | (N)2703.12.1 Where required. (Section deleted) |  |  | no change
2703.12.1.1 Service corridors. An approved emergency alarm system shall be provided in service corridors, with at least one alarm device in the service corridor. | (N)2703.12.1.1 Service corridors. (Section deleted) |  |  | no change
2703.12.1.2 Corridors and interior exit stairways and ramps. Emergency alarms for corridors, interior exit stairways and ramps and exit passageways shall comply with Section 5005.4.4. | (N)2703.12.1.2 Corridors and interior exit stairways and ramps. Emergency alarms for corridors, interior exit stairways and ramps, and exit passageways shall be maintained in accordance with the applicable building code. |  |  | delete
2703.12.1.3 Liquid storage rooms, HPM rooms and gas rooms. Emergency alarms for liquid storage rooms, HPM rooms and gas rooms shall comply with Section 5004.9. | (N)2703.12.1.3 Liquid storage rooms, HPM rooms and gas rooms. Emergency alarms for liquid storage rooms, HPM rooms, and gas rooms shall be maintained in accordance with the applicable building code. |  |  | delete
2703.12.2 Alarm-initiating devices. An approved emergency telephone system, local alarm manual pull stations, or other approved alarm-initiating devices are allowed to be used as emergency alarm-initiating devices. | (N)2703.12.2 Alarm-initiating devices. (Section deleted) |  |  | no change
2703.12.3 Alarm signals. Activation of the emergency alarm system shall sound a local alarm and transmit a signal to the emergency control station. | (N)2703.12.3 Alarm signals. (Section deleted) |  |  | no change
2703.13 Continuous gas detection systems. A continuous gas detection system shall be provided for HPM gases when the physiological warning threshold level of the gas is at a higher level than the accepted permissible exposure limit (PEL) for the gas and for flammable gases in accordance with Sections 2703.13.1 through 2703.13.2.2. | (N)2703.13 Continuous gas detection systems. Continuous gas detection systems shall be maintained in accordance with the applicable building code. |  |  | 2703.13 Continuous gas detection systems. Where provided, a continuous gas detection system shall be maintained for HPM gases. Such a system shall remain in accordance with the applicable building code where the physiological warning threshold level of the gas is at a higher level than the accepted permissible exposure limit (PEL) for the gas and for flammable gases.
2703.13.1 Where required. A continuous gas detection system shall be provided in the areas identified in Sections 2703.13.1.1 through 2703.13.1.4. | (N)2703.13.1 Where required. (Section deleted) |  |  | no change
2703.13.1.1 Fabrication areas. A continuous gas detection system shall be provided in fabrication areas when gas is used in the fabrication area. | (N)2703.13.1.1 Fabrication areas. (Section deleted) |  |  | no change
2703.13.1.2 HPM rooms. A continuous gas detection system shall be provided in HPM rooms when gas is used in the room. | (N)2703.13.1.2 HPM rooms. (Section deleted) |  |  | no change
2703.13.1.3 Gas cabinets, exhausted enclosures and gas rooms. A continuous gas detection system shall be provided in gas cabinets and exhausted enclosures. A continuous gas detection system shall be provided in gas rooms when gases are not located in gas cabinets or exhausted enclosures. | (N)2703.13.1.3 Gas cabinets, exhausted enclosures and gas rooms. (Section deleted) |  |  | no change
2703.13.1.4 Corridors. When gases are transported in piping placed within the space defined by the walls of a corridor and the floor or roof above the corridor, a continuous gas detection system shall be provided where piping is located and in the corridor. Exception: A continuous gas detection system is not required for occasional transverse crossings of the corridors by supply piping which is enclosed in a ferrous pipe or tube for the width of the corridor. | (N)2703.13.1.4 Corridors. (Section deleted) |  |  | no change
2703.13.2 Gas detection system operation. The continuous gas detection system shall be capable of monitoring the room, area or equipment in which the gas is located at or below all the following gas concentrations: 1.Immediately dangerous to life and health (IDLH) values when the monitoring point is within an exhausted enclosure, ventilated enclosure or gas cabinet. 2.Permissible exposure limit (PEL) levels when the monitoring point is in an area outside an exhausted enclosure, ventilated enclosure or gas cabinet. 3.For flammable gases, the monitoring detection threshold level shall be vapor concentrations in excess of 25 percent of the lower flammable limit (LFL) when the monitoring is within or outside an exhausted enclosure, ventilated enclosure or gas cabinet. 4.Except as noted in this section, monitoring for highly toxic and toxic gases shall also comply with Chapter 60. | (N)2703.13.2 Gas detection system operation. (Section deleted) |  |  | 2703.13.2 Gas detection system operation. In accordance with the applicable building code, a continuous gas detection system shall be maintained capable of monitoring the room, area or equipment in which the gas is located at or below all the following gas concentrations: 1.Immediately dangerous to life and health (IDLH) values when the monitoring point is within an exhausted enclosure, ventilated enclosure or gas cabinet. 2.Permissible exposure limit (PEL) levels when the monitoring point is in an area outside an exhausted enclosure, ventilated enclosure or gas cabinet. 3.For flammable gases, the monitoring detection threshold level shall be vapor concentrations in excess of 25 percent of the lower flammable limit (LFL) when the monitoring is within or outside an exhausted enclosure, ventilated enclosure or gas cabinet. 4.Except as noted in this section, monitoring for highly toxic and toxic gases shall also comply with Chapter 60.
2703.13.2.1 Alarms. The gas detection system shall initiate a local alarm and transmit a signal to the emergency control station when a short-term hazard condition is detected. The alarm shall be both visible and audible and shall provide warning both inside and outside the area where the gas is detected. The audible alarm shall be distinct from all other alarms. | (N)2703.13.2.1 Alarms. (Section deleted) |  |  | no change
2703.14 Exhaust ventilation systems for HPM. Exhaust ventilation systems and materials for exhaust ducts utilized for the exhaust of HPM shall comply with Sections 2703.14.1 through 2703.14.3, other applicable provisions of this code, the International Building Code and the International Mechanical Code. | (N)2703.14 Exhaust ventilation systems for HPM. Exhaust ventilation systems and materials for exhaust ducts utilized for the exhaust of HPM shall be maintained in accordance with the applicable building code. |  |  | 2703.14 Exhaust ventilation systems for HPM. Exhaust ventilation systems and materials for exhaust ducts utilized for the exhaust of HPM shall be maintained in accordance with this chapter, other applicable provisions of this code, and remain in accordance with the applicable building code.
2703.14.1 Where required. Exhaust ventilation systems shall be provided in the following locations in accordance with the requirements of this section and the International Building Code: 1.Fabrication areas: Exhaust ventilation for fabrication areas shall comply with the International Building Code. The fire code official is authorized to require additional manual control switches. 2.Workstations: A ventilation system shall be provided to capture and exhaust gases, fumes and vapors at workstations. 3.Liquid storage rooms: Exhaust ventilation for liquid storage rooms shall comply with Section 5004.3.1 and the International Building Code. 4.HPM rooms: Exhaust ventilation for HPM rooms shall comply with Section 5004.3.1 and the International Building Code. 5.Gas cabinets: Exhaust ventilation for gas cabinets shall comply with Section 5003.8.6.2. The gas cabinet ventilation system is allowed to connect to a workstation ventilation system. Exhaust ventilation for gas cabinets containing highly toxic or toxic gases shall also comply with Chapter 60. 6.Exhausted enclosures: Exhaust ventilation for exhausted enclosures shall comply with Section 5003.8.5.2. Exhaust ventilation for exhausted enclosures containing highly toxic or toxic gases shall also comply with Chapter 60. 7.Gas rooms: Exhaust ventilation for gas rooms shall comply with Section 5003.8.4.2. Exhaust ventilation for gas rooms containing highly toxic or toxic gases shall also comply with Chapter 60. 8.Cabinets containing pyrophoric liquids or Class 3 water-reactive liquids: Exhaust ventilation for cabinets in fabrication areas containing pyrophoric liquids or Class 3 water-reactive liquids shall be as required in Section 2705.2.3.4. | (N)2703.14.1 Where required. (Section deleted) |  |  | no change
2703.14.2 Penetrations. Exhaust ducts penetrating fire barriers constructed in accordance with Section 707 of the International Building Code or horizontal assemblies constructed in accordance with Section 711 of the International Building Code shall be contained in a shaft of equivalent fire-resistance-rated construction. Exhaust ducts shall not penetrate fire walls. Fire dampers shall not be installed in exhaust ducts. | (N)2703.14.2 Penetrations. (Section deleted) |  |  | no change
2703.15 Emergency power system. An emergency power system shall be provided in Group H-5 occupancies where required by Section 604. The emergency power system shall be designed to supply power automatically to required electrical systems when the normal supply system is interrupted. | (N)2703.15 Emergency power system. Emergency power system systems shall be maintained in accordance with the applicable building code. |  |  | 2703.15 Emergency power system. An emergency power system shall be maintained in Group H-5 occupancies in accordance with Section 604. The emergency power system shall be maintained to supply power automatically to required electrical systems when the normal supply system is interrupted.
2703.15.1 Required electrical systems. Emergency power shall be provided for electrically operated equipment and connected control circuits for the following systems: 1.HPM exhaust ventilation systems. 2.HPM gas cabinet ventilation systems. 3.HPM exhausted enclosure ventilation systems. 4.HPM gas room ventilation systems. 5.HPM gas detection systems. 6.Emergency alarm systems. 7.Manual fire alarm systems. 8.Automatic sprinkler system monitoring and alarm systems. 9.Automatic alarm and detection systems for pyrophoric liquids and Class 3 water-reactive liquids required in Section 2705.2.3.4. 10.Flow alarm switches for pyrophoric liquids and Class 3 water-reactive liquids cabinet exhaust ventilation systems required in Section 2705.2.3.4. 11.Electrically operated systems required elsewhere in this code or in the International Building Code applicable to the use, storage or handling of HPM. | (N)2703.15.1 Required electrical systems. (Section deleted) |  |  | 2703.15.1 Required electrical systems. Where provided or required by the applicable building code, emergency power shall be maintained for electrically operated equipment and connected control circuits for the following systems: 1.HPM exhaust ventilation systems. 2.HPM gas cabinet ventilation systems. 3.HPM exhausted enclosure ventilation systems. 4.HPM gas room ventilation systems. 5.HPM gas detection systems. 6.Emergency alarm systems. 7.Manual fire alarm systems. 8.Automatic sprinkler system monitoring and alarm systems. 9.Automatic alarm and detection systems for pyrophoric liquids and Class 3 water-reactive liquids required in Section 2705.2.3.4. 10.Flow alarm switches for pyrophoric liquids and Class 3 water-reactive liquids cabinet exhaust ventilation systems required in Section 2705.2.3.4. 11.Electrically operated systems required elsewhere in this code or in the applicable building code that are applicable to the use, storage or handling of HPM.
2703.15.2 Exhaust ventilation systems. Exhaust ventilation systems are allowed to be designed to operate at not less than one-half the normal fan speed on the emergency power system when it is demonstrated that the level of exhaust will maintain a safe atmosphere. | (N)2703.15.2 Exhaust ventilation systems. Exhaust ventilation systems shall be maintained in accordance with the applicable building code. |  |  | 2703.15.2 Exhaust ventilation systems. Exhaust ventilation systems are allowed to be maintained to operate at not less than one-half the normal fan speed on the emergency power system when it is demonstrated that the level of exhaust will maintain a safe atmosphere.
2703.16 Sub-atmospheric pressure gas systems. Sub-atmospheric pressure gas systems (SAGS) shall be in accordance with NFPA 318. | (N)2703.16 Subatmospheric pressure gas systems. Subatmospheric pressure gas systems (SAGS) shall be maintained in accordance with the applicable building code. |  |  | 2703.16 Sub-atmospheric pressure gas systems. Sub-atmospheric pressure gas systems (SAGS) shall be maintained in accordance with NFPA 318 and remain in accordance with the applicable building code.
2704.1 General. Storage of hazardous materials shall comply with Section 2703 and this section and other applicable provisions of this code. | (N)2704.1 General. Storage of hazardous materials shall comply with Section 2703 and this section and other applicable provisions of this code to the extent that such requirements are operational in nature and do not affect how a building is constructed. |  |  | 2704.1 General. Storage of hazardous materials shall comply with Section 2703 and this section and other applicable provisions of this code.
2704.2.1 Location of HPM storage in fabrication areas. Storage of HPM in fabrication areas shall be within approved or listed storage cabinets, gas cabinets, exhausted enclosures or within a workstation as follows. 1.Flammable and combustible liquid storage cabinets shall comply with Section 5704.3.2. 2.Hazardous materials storage cabinets shall comply with Section 5003.8.7. 3.Gas cabinets shall comply with Section 5003.8.6. Gas cabinets for highly toxic or toxic gases shall also comply with Section 6004.1.2. 4.Exhausted enclosures shall comply with Section 5003.8.5. Exhausted enclosures for highly toxic or toxic gases shall also comply with Section 6004.1.3. 5.Workstations shall comply with Section 2705.2.3. | 2704.2.2.1 Storage and use in fabrication areas. The maximum quantities of hazardous materials stored or used in a single fabrication area shall not exceed the quantities set forth by the applicable building code. |  |  | 2704.2.1 Location of HPM storage in fabrication areas. Storage of HPM in fabrication areas shall be maintained within approved or listed storage cabinets, gas cabinets, exhausted enclosures or within a workstation as follows. 1.Flammable and combustible liquid storage cabinets shall comply with Section 5704.3.2. 2.Hazardous materials storage cabinets shall comply with Section 5003.8.7. 3.Gas cabinets shall comply with Section 5003.8.6. Gas cabinets for highly toxic or toxic gases shall also comply with Section 6004.1.2. 4.Exhausted enclosures shall comply with Section 5003.8.5. Exhausted enclosures for highly toxic or toxic gases shall also comply with Section 6004.1.3. 5.Workstations shall comply with Section 2705.2.3.
2704.2.2.1 Storage and use in fabrication areas. The maximum quantities of hazardous materials stored or used in a single fabrication area shall not exceed the quantities set forth in Table 2704.2.2.1. TABLE 2704.2.2.1 QUANTITY LIMITS FOR HAZARDOUS MATERIALS IN A SINGLE FABRICATION AREA IN GROUP H-5a | (N)TABLE 2704.2.2.1 QUANTITY LIMITS FOR HAZARDOUS MATERIALS IN A SINGLE FABRICATION AREA IN GROUP H-5 (Table deleted) |  |  | 2704.2.2.1 Storage and use in fabrication areas. The maximum quantities of hazardous materials stored or used in a single fabrication area shall not exceed the quantities set forth in Table 2704.2.2.1. TABLE 2704.2.2.1 QUANTITY LIMITS FOR HAZARDOUS MATERIALS IN A SINGLE FABRICATION AREA IN GROUP H-5a
2704.3.1 HPM storage. The indoor storage of HPM in quantities greater than those listed in Sections 5003.1.1 and 3404.3.4 shall be in a room complying with the requirements of the International Building Code and this code for a liquid storage room, HPM room or gas room as appropriate for the materials stored. | 2704.3.1 HPM storage. The indoor storage of HPM in quantities greater than those listed in Sections 5003.1.1 and 3404.3.4 shall be in a room complying with the requirements of this code for a liquid storage room, HPM room, or gas room as appropriate for the materials stored. |  |  | 2704.3.1 HPM storage. The indoor storage of HPM in quantities greater than those listed in Sections 5003.1.1 and 3404.3.4 shall be in a room complying with the requirements of the applicable building code and this code for a liquid storage room, HPM room or gas room as appropriate for the materials stored.
2705.1 General. The use and handling of hazardous materials shall comply with this section, Section 2703 and other applicable provisions of this code. | 2705.1 General. The use and handling of hazardous materials shall comply with this section, Section 2703, and other applicable provisions of this code to the extent that such requirements are operational in nature and do not affect how a building is constructed. |  |  | 2705.1 General. The use and handling of hazardous materials shall comply with this section, Section 2703 and other applicable provisions of this code.
2705.2.3.2 Protection of vessels. Vessels containing hazardous materials located in or connected to a workstation shall be protected as follows: 1.HPM: Vessels containing HPM shall be protected from physical damage and shall not project from the workstation. 2.Hazardous cryogenic fluids, gases and liquids: Hazardous cryogenic fluid, gas and liquid vessels located within a workstation shall be protected from seismic forces in an approved manner in accordance with the International Building Code. 3.Compressed gases: Protection for compressed gas vessels shall also comply with Section 5303.5. 4.Cryogenic fluids: Protection for cryogenic fluid vessels shall also comply with Section 5503.5. | (N)2705.2.3.2 Protection of vessels. Vessels containing hazardous materials located in or connected to a workstation shall be protected as follows: 1. HPM: Vessels containing HPM shall be protected from physical damage and shall not project from the workstation. 2. Compressed gases: Protection for compressed gas vessels shall also comply with Section 5303.5. 3. Cryogenic fluids: Protection for cryogenic fluid vessels shall also comply with Section 5503.5. |  |  | no change
2705.3.1 Corridors and enclosures for stairways and ramps. Corridors and enclosures for exit stairways and ramps in new buildings or serving new fabrication areas shall not contain HPM, except as permitted in corridors by Section 415.10.6.4 of the International Building Code and Section 2705.3.2 of this code. | (N)2705.3.1 Corridors and enclosures for stairways and ramps. Corridors and enclosures for exit stairways and ramps in new fabrication areas shall not contain HPM, except as permitted in corridors by Section 2705.3.2 and the applicable building code. |  |  | no change
2705.3.2.1 Fabrication area alterations. When existing fabrication areas are altered or modified in existing buildings, HPM is allowed to be transported in existing corridors when such corridors comply with Section 5003.10 of this code and Section 415.10.2 of the International Building Code. | 2705.3.2.1 Fabrication area alterations. Where existing fabrication areas are altered or modified in existing buildings, HPM is allowed to be transported in existing corridors where such corridors comply with the applicable building code. |  |  | 2705.3.2.1 Fabrication area alterations. When existing fabrication areas are altered or modified in existing buildings, HPM is allowed to be transported in existing corridors when such corridors comply with Section 5003.10 of this code and the applicable building code.
2705.3.3 Service corridors. When a new fabrication area is constructed, a service corridor shall be provided where it is necessary to transport HPM from a liquid storage room, HPM room, gas room or from the outside of a building to the perimeter wall of a fabrication area. Service corridors shall be designed and constructed in accordance with the International Building Code. | (N)2705.3.3 Service corridors. (Section deleted) |  |  | 2705.3.3 Service corridors. Where it is necessary to transport HPM from a liquid storage room, HPM room, gas room or from the outside of a building to the perimeter wall of a fabrication area, such transport shall be through service corridors approved in accordance with the applicable building code.

## Ch28 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
2801.2 Permit. Permits shall be required as set forth in Section 107.2. | 2801.2 Permit. Permits shall be required as set forth in Section 107.2. |  |  | no change
2803.1 Open yards. Open yards required by the International Building Code shall be maintained around structures. | (N)2803.1 Open yards. Open yards around structures required by the applicable building code shall be maintained. |  |  | 2803.1 Open yards. Open yards required by the applicable building code shall be maintained around structures. The space shall be maintained free of obstructions associated with the outdoor storage of the materials regulated by Chapter 28, which could interfere with the function of the open space, especially that of providing fire department access to the building. |  | There are no maintenance requirements in the building code. The building code requires that certain buildings face an open space on at least one side. The open spaces may be a yard required for the purpose of providing light and ventilation or they may be a public way provided in order to achieve an increase in building area called a “frontage increase”, or to allow a building to be considered an “unlimited area building” . Regardless of the purpose of the open space, this section requires that the space be maintained and be free of obstructions associated with the outdoor storage of the materials regulated by Chapter 28, which could interfere with the function of the open space, especially that of providing fire department access to the building.
2803.2 Dust control. Equipment or machinery located inside buildings that generates or emits combustible dust shall be provided with an approved dust collection and exhaust system installed in accordance with Chapter 22 and the International Mechanical Code. Equipment or systems that are used to collect, process or convey combustible dusts shall be provided with an approved explosion control system. | (N)2803.2 Dust control. Equipment or machinery located inside buildings that generates or emits combustible dust equipped with an approved dust collection and exhaust system shall be maintained in accordance with the applicable building code. Equipment or systems that are used to collect, process or convey combustible dusts shall be provided with an approved explosion control system. |  |  | Equipment or machinery located inside buildings that generates or emits combustible dust shall be provided with an approved dust collection and exhaust system installed in accordance with Chapter 22 and the applicable building code. Equipment or systems that are used to collect, process or convey combustible dusts shall maintain an approved explosion control system installed in accordance with the applicable building code and maintained in accordance with Chapter 9. |  | There are no maintenance requirements for dust control in the building code. The basic wood-processing activities related to lumber yards and woodworking facilities generate large volumes of wood particles suspended in the air, creating a potentially explosive form of dust. Where such activities are located inside of buildings, this section requires that combustible dust be controlled by an approved dust-collection and exhaust system designed and installed in accordance with IFC Chapter 22, and the building code. There are two basic designs of dust collection systems. One is a single-stage system that consists of a single dust collector in the form of a cyclone separator or a combination cyclone/baghouse unit. The other is a two-stage system that consists of a cyclone separator followed by a bag-type filter house. An approved explosion control system is also required to be maintained for the equipment and systems that collect and convey the combustible dust. Such systems should be maintained in accordance with Section 911.
2803.2.1 Explosion venting. Where a dust explosion hazard exists in equipment rooms, buildings or other enclosures, such areas shall be provided with explosion (deflagration) venting or an approved explosion suppression system complying with Section 911. | (N)2803.2.1 Explosion venting. Explosion venting required for dust explosion hazards shall be maintained in accordance with the applicable building code. |  |  | Where a dust explosion hazard exists in equipment rooms, buildings or other enclosures, such areas shall be declared an unsafe condition in accordance with Section 110.1 and operations shall not be continued until the hazard is mitigated. Where explosion venting is provided it shall be maintained in accordance with this Chapter 9 and the applicable buidling code. |  | The intent of this section is not maintenance of the explosion venting system as indicated in the 2015 VSFPC, but rather identifying unprotected dust explosion hazards. When wood dust is ignited while suspended in air in concentrations above the minimum combustible concentration (MCC), it burns violently, producing a deflagration. This likelihood depends on the concentration of fuel per unit volume. Most of the time, dust-collection systems remove the larger dust particles, allowing the finer particles to pass through the system and reenter the production area. The finer dust can create an explosion and fire hazard unless an approved suppression system is used.
2803.3 Waste removal. Sawmills, planning mills and other woodworking plants shall be equipped with a waste removal system that will collect and remove sawdust and shavings. Such systems shall be installed in accordance with Chapter 22 and the International Mechanical Code. Exception: Manual waste removal when approved. | (N)2803.3 Waste removal. Waste removal systems required for sawmills, planning mills and other woodworking plants shall be maintained in accordance with the applicable building code. Exception: Manual waste removal where approved. |  |  | 2803.3 Waste removal. Sawmills, planning mills and other woodworking plants shall maintain waste removal systems that collect and remove sawdust and shavings. Such systems shall be maintained in accordance with Chapter 22 and comply with the applicable building code. Exception: Manual waste removal when approved. |  | There are not any maintenance requirements in the building code. Like many other organic materials, sawdust, wood chips and other similar waste materials are susceptible to spontaneous heat. Pilings and debris must be turned over or consumed regularly to minimize the potential for spontaneous combustion. Some waste material is used as fuel and some might go to pulp or particleboard manufacturers. Finer material is removed by air-moving equipment, cyclones or air bags. Chapter 22 and the IMC give the requirements for waste removal systems.
2803.4 Electrical equipment. Electrical wiring and equipment shall comply with NFPA 70. | (N)2803.4 Electrical equipment. Electrical wiring and equipment shall be maintained in accordance with the applicable building code |  |  | 2803.4 Electrical equipment Electrical wiring and equipment shall be maintained in accordance with Chapter 6, NFPA 70, and the applicable building code. |  | There are not any maintenance requirements in the building code. Arcs, sparks and loose connections often supply the ignition source that a vapor or combustible material needs for fire. Electrical equipment must be listed for the use it is installed for and comply with the requirements of NFPA 70.
2804.2 Fire alarms. An approved means for transmitting alarms to the fire department shall be provided in timber and lumber production mills and plywood and veneer mills. | (N)2804.2 Fire alarms. Where provided, fire alarms maintained in accordance with the applicable building code. |  |  | 2804.2 Fire alarms. Where provided, fire alarm systems shall be maintained in accordance with Chapter 9. |  | There are not any fire alarm maintenance requirements in the building code.
2804.2.1 Manual fire alarms. A manual fire alarm system complying with Section 907.2 shall be installed in areas of timber and lumber production mills and for plywood and veneer mills that contain product dryers. Exception: Where dryers or other sources of ignition are protected by a supervised automatic sprinkler system complying with Section 903. | (N)2804.2.1 Manual fire alarms. Where installed, manual fire alarm systems shall be maintained in accordance with the applicable building code. |  |  | 2804.2.1 Delete |  | This section is unnecessary since 2804.2 covers fire alarm device maintenance.
2804.4 Automatic sprinkler systems. Automatic sprinkler systems shall be installed in accordance with Section 903.3.1.1. | (N)2804.4 Automatic sprinkler systems. Automatic sprinkler systems shall be maintained in accordance with the applicable building code. |  |  | 2804.4 Automatic sprinkler systems. Automatic sprinkler systems shall be maintained in accordance with Chapter 9. |  | There are not any fire sprinkler maintenance requirements in the building code.
2805.2 Dryer protection. Dryers shall be protected throughout by an approved, automatic deluge water-spray suppression system complying with Chapter 9. Deluge heads shall be inspected quarterly for pitch buildup. Deluge heads shall be flushed during regular maintenance for functional operation. Manual activation valves shall be located within 75 feet (22 860 mm) of the drying equipment. | (N)2805.2 Dryer protection. Dryers shall be maintained in accordance with the applicable building code. Deluge heads shall be inspected quarterly for pitch buildup. Deluge heads in dryers shall be flushed during regular maintenance for functional operation. |  |  | 2805.2 Dryer protection. Dryers protected by an approved, automatic deluge water-spray suppression system shall be maintained in accordance with Chapter 9. Deluge heads shall be inspected quarterly for pitch buildup. Deluge heads shall be flushed during regular maintenance for functional operation. |  | There are not any fire sprinkler maintenance requirements in the building code.
2807.2 Size of piles. Piles shall not exceed 60 feet (18 288 mm) in height, 300 feet (91 440 mm) in width and 500 feet (152 m) in length. Piles shall be separated from adjacent piles or other exposures by approved fire apparatus access roads. Exception: The fire code official is authorized to allow the pile size to be increased when additional fire protection is provided in accordance with Chapter 9. The increase shall be based on the capabilities of the system installed. | 2807.2 Size of piles. Piles shall not exceed 60 feet (18 288 mm) in height, 300 feet (91 440 mm) in width, and 500 feet (152 m) in length. Piles shall be separated from adjacent piles or other exposures by approved fire apparatus access roads. Exception: The fire code official is authorized to allow the pile size to be increased where additional approved fire protection is provided in accordance with Chapter 9. |  |  | no change
2807.3 Pile fire protection. Automatic sprinkler protection shall be provided in conveyor tunnels and combustible enclosures that pass under a pile. Combustible or enclosed conveyor systems shall be equipped with an approved automatic sprinkler system. | (N)2807.3 Pile fire protection. Automatic sprinkler protection provided in conveyor tunnels and combustible enclosures that pass under a pile shall be maintained in accordance with the applicable building code. |  | this is processing equipmen that is exempt from the buidling code. Hence the BO is not the AHJ to require the installation,but is to permit and oversee the installation(?) | 2807.3 Outdoor pile fire protection. Where conveyor tunnels and combustible enclosures that pass under an outdoor pile, automatic sprinkler protection shall be provided. Automatic sprinkler protection shall be maintained in accordance with Chapter 9. |  | This requiment addresses outdoor pile processing equipment that is not within a building and believed to be exempt from the building code. Unless found to be regulated by the building code, it would be regulated by the Fire Prevention Code. Automatic sprinklers are needed because of the difficulty of manual fire suppression operations in concealed, enclosed and elevated outdoor areas.
2808.7 Pile fire protection. Automatic sprinkler protection shall be provided in conveyor tunnels and combustible enclosures that pass under a pile. Combustible conveyor systems and enclosed conveyor systems shall be equipped with an approved automatic sprinkler system. | (N)2808.7 Pile fire protection. Automatic sprinkler protection provided in conveyor tunnels and combustible enclosures that pass under a pile shall be maintained in accordance with the applicable building code. |  | Outdoor or indoor or both | 2808.7 Pile fire protection. Automatic sprinkler protection shall be provided in conveyor tunnels and combustible enclosures that pass under a pile. Combustible conveyor systems and enclosed conveyor systems shall be equipped with an approved automatic sprinkler system.These systems shall be maintained in accordance with Chapter 9. |  | This requiment addresses outdoor pile processing equipment that is not within a building and believed to be exempt from the building code. Unless found to be regulated by the building code, it would be regulated by the Fire Prevention Code. Automatic sprinklers are needed because of the difficulty of manual fire suppression operations in concealed, enclosed and elevated outdoor areas.

## Ch29
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
2901.2 Permits. Permits shall be required as set forth in Section 107.2. | 2901.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
2903.1 Building features. Manufacturing of organic coatings shall be done only in buildings that do not have pits or basements. | (N)2903.1 Building features. (Section deleted) |  |  | 2903.1 Building Features. Unless approved by the applicable building code, manufacturing of organic coatings shall be done only in buildings that do not have pits or basements. |  | The use of organic coating processes are not a specificialy approved use group classificaiton in the IBC and therefore it is imprtant to provide context as to where these operations should and should not be conducted. The IBC classifies organic coating processes in Group H-2 or H-3 occupancies, depending on the types and amounts of materials, when the maximum allowable quantity per control area (MAQ) of hazardous materials in Table 307.1(1) of that code is exceeded. Basements, pits or depressed first-floor construction are prohibited because of the tendency for hazardous materials vapors to accumulate in low areas and the difficulty in fighting fires in such areas and occupancies.
2903.2 Location. Organic coating manufacturing operations and operations incidental to or connected with organic coating manufacturing shall not be located in buildings having other occupancies. | (N)2903.2 Location. (Section deleted) |  | Provides a pointer to the applicable building code for approval of hazardous locations. | 2903.2 Location. Unless approved by the applicable building code, organic coating manufacturing operations and operations incidental to or connected with organic coating manufacturing shall not be located in buildings having other occupancies. |  | The use of organic coating processes are not a specificialy approved use group classificaiton in the IBC and therefore it is imprtant to provide context as to where these operations should and should not be conducted. The IBC classifies organic coating processes in Group H-2 or H-3 occupancies, depending on the types and amounts of materials, when the maximum allowable quantity per control area (MAQ) of hazardous materials in Table 307.1(1) of that code is exceeded. Incidental occupancies involve operations and activities closely related to the primary occupancy and are necessary for efficient, continuous and safe organic coatings manufacture. Administration, storage, shipping and receiving, as well as other related but not indispensable operations, should be located in separate buildings. Separations must have a fire-resistance rating, separation distance or a combination of the two as required by the IBC.
2903.4 Fire protection systems. Fire protection systems shall be installed, maintained, periodically inspected and tested in accordance with Chapter 9. | 2903.4 Fire protection systems. Fire protection systems shall be maintained, periodically inspected, and tested in accordance with Chapter 9. |  |  | no change
2903.10 Drainage. Drainage facilities shall be provided to direct flammable and combustible liquid leakage and fire protection water to an approved location away from the building, any other structure, storage area or adjoining premises. | 2903.10 Drainage. Drainage facilities shall be maintained to direct flammable and combustible liquid leakage and fire protection water to an approved location away from the building, any other structure, any storage area, or adjoining premises. |  |  | no change
2903.11 Alarm system. An approved fire alarm system shall be provided in accordance with Section 907. | (N)2903.11 Alarm system. Alarm systems shall be maintained in accordance with the applicable building code. |  |  | 2903.11 Alarm system. Alarm systems shall be maintained in accordance with Chapter 9. |  | There are no maintenance requirements for fire alarm systems in the building code.
2904.1 Wiring and equipment. Electrical wiring and equipment shall comply with this chapter and shall be installed in accordance with NFPA 70. | (N)2904.1 Wiring and equipment. Electrical wiring and equipment shall be maintained in accordance with the applicable building code. |  |  | 2904.1 Wiring and equipment. Electrical wiring and equipment shall be maintained in accordance with this chapter, chapter 6 and NFPA 70. |  | There are no maintenance requirements in the building code. NFPA 70 and the requirements of this section apply to electrical wiring and equipment to reduce the fire hazard associated with the presence of such equipment in areas where organic coatings are being manufactured..
2904.3 Bonding. Equipment including, but not limited to, tanks, machinery and piping, shall be bonded and connected to a ground where an ignitable mixture is capable of being present. | (N)2904.3 Bonding. Bonding provided for equipment including tanks, machinery and piping shall be maintained in accordance with the applicable building code. |  | Nearly identical to the 1978 BOCA and maintains operational language regarding ignitable mixture being present | 2904.3 Bonding. Equipment including, but not limited to, tanks, machinery and piping, shall not be operated where an ignitable mixture is capable of being present unless bonded and connected to a ground in acordance with the appliable building code. |  | Bonding and grounding is an operational requirement not construction. This section is nearly identical to the 1978 BOCA and maintains operational language regarding ignitable mixtures being present.
2904.3.1 Piping. Electrically isolated sections of metallic piping or equipment shall be grounded or bonded to the other grounded portions of the system. | (N)2904.3.1 Piping. Electrically isolated sections of metallic piping or equipment shall be maintained in accordance with the applicable building code. |  |  | 2904.3.1 Piping. Electrically isolated sections of metallic piping or equipment shall be maintained grounded or bonded to the other grounded portions of the system in accordance with the appliable building code. |  | This section does not require maintenance of piping as indicated in the 2015VSFPC but rather bonding and grounding. In order to maintain the continuity of the grounding path for all portions of a tank and piping system that do not form a continuous conductive path, each electrically isolated section of piping must be independently grounded or, alternatively, be bonded to another properly grounded portion of the system.
2904.4 Ground. Metal framing of buildings shall be grounded with resistance of not more than 5 ohms. | (N)2904.4 Ground. Metal framing of buildings shall be grounded in accordance with the applicable building code. |  |  | No change
2905.1 Design. Process structures shall be designed and constructed in accordance with the International Building Code. | (N)2905.1 Design. (Section deleted) |  |  | 2905.1 Process Location. Process operations shall be conducted in structures approved in accordance with the applicable building code. |  | The use of organic coating processes are not a specificialy approved use group classificaiton in the IBC and therefore it is imprtant to provide context as to where these operations should and should not be conducted. The IBC classifies organic coating processes in occupancy Group H-2 or H-3, depending on the type and amounts of materials, when the MAQ of hazardous materials in Table 307.1(1) of that code is exceeded. IBC Section 418 further regulates these structures as to their physical configuration, location and finished product storage. See the commentary to IBC Sections 418.1 through 418.6 for further information.
2905.4 Explosion control. Explosion control shall be provided in areas subject to potential deflagration hazards as indicated in NFPA 35. Explosion control shall be provided in accordance with Section 911. | (N)2905.4 Explosion control. Explosion control shall be maintained in accordance with the applicable building code and maintenance provisions of NFPA 35. |  |  | 2905.4 Explosion control. Explosion control shall be maintained in areas subject to potential deflagration hazards as indicated by the appllicable building code. Explosion control shall be maintained in accordance with Section 911 and NFPA 35. |  | This intent of this section is to identify where explosion control would be needed due to the operations present. Explosion control is required where Class I liquids or flammable dusts create a potential deflagration hazard; as defined by NFPA 35. Section 911 and IBC Section 414.5.1 prescribe requirements for explosion control. NFPA 68 also provides guidance on this subject.
2905.5 Ventilation. Enclosed structures in which Class I liquids are processed or handled shall be ventilated at a rate of not less than 1 cubic foot per minute per square foot [0.00508 m3/(s · m2)] of solid floor area. Ventilation shall be accomplished by exhaust fans that take suction at floor levels and discharge to a safe location outside the structure. Noncontaminated intake air shall be introduced in such a manner that all portions of solid floor areas are provided with continuous uniformly distributed air movement. | (N)2905.5 Ventilation. Enclosed structures in which Class I liquids are processed or handled shall be ventilated in accordance with the applicable building code. |  | Consistent back to at least 1978 BOCA | 2905.5 Ventilation. Enclosed structures in which Class I liquids are processed or handled shall be ventilated to a safe location outside of the structure in accordance with the applicable building code. |  | The proposed section includes clear guidance that ventiallation is to be to the atomosphere outside of the enclosure. Ventilation systems must be designed to prevent the accumulation of vapors in the building where Class I flammable liquids are processed. Uncontaminated air, preferably from a source outside the building, should be distributed to dilute and disperse vapors over the entire solid floor area and then discharge them to a safe location outside the building.
2906.1 Mills. Mills, operating with close clearances, which process flammable and heat-sensitive materials, such as nitrocellulose, shall be located in a detached building or in a noncombustible structure without other occupancies. The amount of nitrocellulose or other flammable material brought into the area shall not be more than the amount required for a batch. | (N)2906.1 Mills. Mills operating with close clearances that process flammable and heatsensitive materials, such as nitrocellulose, shall be maintained in accordance with the applicable building code. |  |  | Mills, operating with close clearances, which process flammable and heat-sensitive materials, such as nitrocellulose, shall maintain operations in a detached building or in a noncombustible structure without other occupancies unless otherwise approved by the applicable building code. The amount of nitrocellulose or other flammable material brought into the area shall not be more than the amount required for a batch. |  | There are no maintenance requirements in the building code for operating mills. Milling of heat-sensitive materials, such as nitrocellulose, is an extraordinary hazard that must be located in single-purpose buildings, away from other uses and high-hazard operations. Pebble mills pose a special vapor ignition hazard caused by static electricity. Both the grinding material and inner lining of these mills are made of materials with good insulating characteristics. Because static electricity is produced during milling, it has nowhere to go. Generally, the atmosphere inside of this type of mill is made either partially or totally inert using nitrogen or carbon dioxide gas to prevent ignition.
2909.2 Tank storage. Tank storage for flammable and combustible liquids located inside of structures shall be limited to storage areas at or above grade which are separated from the processing area in accordance with the International Building Code. Processing equipment containing flammable and combustible liquids and storage in quantities essential to the continuity of the operations shall not be prohibited in the processing area. | (N)2909.2 Tank storage. Tank storage for flammable and combustible liquids located inside of structures shall be limited to storage areas at or above grade that are separated from the processing area in accordance with the applicable building code. Processing equipment containing flammable and combustible liquids and storage in quantities essential to the continuity of the operations shall not be prohibited in the processing area. |  |  | no change
2909.4 Nitrocellulose storage. Nitrocellulose storage shall be located on a detached pad or in a separate structure or a room enclosed in accordance with the International Building Code. The nitrocellulose storage area shall not be utilized for any other purpose. Electrical wiring and equipment installed in storage areas adjacent to process areas shall comply with Section 2904.2. | (N)2909.4 Nitrocellulose storage. Nitrocellulose storage shall be located on a detached pad or in a separate structure or a room enclosed in accordance with the applicable building code. |  |  | 2909.4 Nitrocellulose storage. Nitrocellulose storage shall be located on a detached pad or in a separate structure or a room enclosed in accordance with the applicable building code. When nitrocellulose storage is present, the area shall not be utilized for any other use in accordance with the applicable building code. Electrical wiring and equipment in storage areas adjacent to process areas shall be maintained in accordance with Section 2904.2. |  | There are no maintenance requirements in the building code for mitrocellulose storage operations. Solvent-wet nitrocellulose is the most common type associated with lacquer production. In this case, the solvent is usually an alcohol, which is a Class I flammable liquid. Solvent-wet nitrocellulose possesses the same fire-hazard characteristics as the solvent in which it is stored, with important differences noted. Solvent-wet nitrocellulose becomes increasingly unstable as the temperature rises. Once ignited, nitrocellulose will continue to burn even in the absence of oxygen. Therefore, extra diligence must be used to prevent ignition and fire spread. IBC Section 418.5 contains requirements for the separation of these areas.
2909.6 Finished products. Finished products that are flammable or combustible liquids shall be stored outside of structures, in a separate structure, or in a room separated from the processing area in accordance with the International Building Code. The storage of finished products shall be in tanks or closed containers in accordance with Chapter 57. | 2909.6 Finished products. Finished products that are flammable or combustible liquids shall be stored outside of structures, in a separate structure, or in a room separated from the processing area where such storage is permitted under the applicable building code. The storage of finished products shall be in tanks or closed containers in accordance with Chapter 57. |  |  | no change
DRAFT : WORK IN PROGRESS

## Ch30
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
3001.1 Scope. This chapter shall apply to the installation and operation of industrial ovens and furnaces. Industrial ovens and furnaces shall comply with the applicable provisions of NFPA 86, the International Fuel Gas Code, International Mechanical Code and this chapter. The terms “ovens” and “furnaces” are used interchangeably in this chapter. | (N)3001.1 Scope. This chapter shall apply to the maintenance and operation of industrial ovens and furnaces. Industrial ovens and furnaces shall comply with the applicable provisions of NFPA 86 and this chapter. The terms "ovens" and "furnaces" are used interchangeably in this chapter. |  |  | 3001.1 Scope. This chapter shall apply to the maintenance and operation of industrial ovens and furnaces. Industrial ovens and furnaces shall comply with the applicable provisions of NFPA 86, the applicable building code and this chapter. The terms "ovens" and "furnaces" are used interchangeably in this chapter. |  | Restores reference to applicable building code in place of the IFGC and IMC.
3001.2 Permits. Permits shall be required as set forth in Section 107.2. | 3001.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
3003.1 Ventilation. Enclosed rooms or basements containing industrial ovens or furnaces shall be provided with combustion air in accordance with the International Mechanical Code and the International Fuel Gas Code, and with ventilation air in accordance with the International Mechanical Code. | (N)3003.1 Ventilation. Enclosed rooms or basements containing industrial ovens or furnaces shall be maintained in accordance with the applicable building code. |  |  | 3003.1 Ventilation. Enclosed rooms or basements containing industrial ovens or furnaces shall be maintained with combustion air in accordance with the applicable building code, and with ventilation air in accordance with the applicable building code. |  | Maintenance language, not construction. The proposal restores esstential context as to combustion air and ventilation. Placing an oven or furnace below grade presents difficulty in ventilation and offers severe obstacles to proper explosion release. When gas or oil is used, the furnace or oven should be vented separately unless the products of discharge deposit directly into the oven.
3003.4 Temperatures. Roofs and floors of ovens shall be insulated and ventilated to prevent temperatures at combustible ceilings and floors from exceeding 160°F (71°C). | (N)3003.4 Temperatures. (Section deleted) |  | Consistent with the 1978 BOCA | 3003.4 Temperatures. Unless otherwise approved by the applicable building code, roofs and floors of ovens shall maintain insulation and ventilation to prevent temperatures at combustible ceilings and floors from exceeding 160°F (71°C). |  | Temperature regulation is an operational requirement. This section including the temperature critiea goes back until at least the 1978 BOCA. Furnaces and ovens should be maintained to minimize their fire hazard when operating at elevated temperatures. Insulation and ventilation are important in preventing heat transfer from the oven to surrounding combustible products.
3004.1 Fuel-gas piping. Fuel-gas piping serving industrial ovens shall comply with the International Fuel Gas Code. Piping for other fuel sources shall comply with this section. | (N)3004.1 Fuel-gas piping. Fuel-gas piping serving industrial ovens shall be maintained in accordance with the applicable building code. |  |  | 3004.1 Fuel piping. Fuel piping serving industrial ovens shall be maintained in accordance with this section and remain in accordance with the applicable building code. |  | There are no maintenance requirements in the building code. Electrically wired, oil-fired and special-atmosphere furnaces are covered in this section. Fuel-gas piping is covered in the IFGC
3004.2 Shutoff valves. Each industrial oven or furnace shall be provided with an approved manual fuel shutoff valve in accordance with the International Mechanical Code or the International Fuel Gas Code. | (N)3004.2 Shutoff valves. (Section deleted) |  |  | 3004.2 Shutoff valves. Manual fuel shutoff valves for industrial ovens or furnaces shall be maintained and remain in accordance with the applicable building code. |  | Shutoff valves need to be maintained. Individual manual shutoff valves are used for equipment isolation.
3004.2.1 Fuel supply lines. Valves for fuel supply lines shall be located within 6 feet (1829 mm) of the appliance served. Exception: When approved and the valve is located in the same general area as the appliance served. | (N)3004.2.1 Fuel supply lines. Valves for fuel supply lines shall be maintained in accordance with the applicable building code. |  | The 6ft criteria has been in the codes since 2000 | 3004.2.1 Fuel supply lines. Valves for fuel supply lines shall be located within 6 feet (1829 mm) of the appliance served. Exception: When approved and the valve is located in the same general area as the appliance served. |  | The placement and operation of emergency shutoff valves is and operational challenge. A fuel supply shutoff valve must be maintained in the fuel supply line within 6 feet (1829 mm) of the appliance for easy shutoff of fuel in case of an emergency.
None | (N)3004.3 Valve Position. (Section deleted) |  | Add additional language from IFC | 3004.3Valve position. Manual fuel shutoff valves shall be maintained to visually indicate the open or closed position of the valve. Manual fuel shutoff valves shall not be equipped with removable handles or wrenches unless the handle or wrench can only be installed parallel with the fuel line when the valve is in the open position.
3005.1 Shut down. Interlocks shall be provided for Class A ovens so that conveyors or sources of flammable or combustible materials shall shut down if either the exhaust or recirculation air supply fails. | (N)3005.1 Shut down. Interlocks shall be maintained in accordance with the applicable building code. |  | Consistent with the 1978 BOCA | 3005.1 Shut down. Interlocks shall be provided for Class A ovens so that conveyors or sources of flammable or combustible materials shall shut down if either the exhaust or recirculation air supply fails
3006.1 Required protection. Class A and B ovens which contain, or are utilized for the processing of, combustible materials shall be protected by an approved automatic fire-extinguishing system complying with Chapter 9. | (N)3006.1 Required protection. Fireextinguishing systems provided for Classes A and B ovens that contain, or are utilized for the processing of, combustible materials shall be maintained in accordance with the applicable building code. |  |  | 3006.1 Required protection. Fire extinguishing systems provided for Classes A and B ovens that contain, or are utilized for the processing of, combustible materials shall be maintained in accordance with chapter 9.
3006.2 Fixed fire-extinguishing systems. Fixed fire-extinguishing systems shall be provided for Class C or D ovens to protect against such hazards as overheating, spillage of molten salts or metals, quench tanks, ignition of hydraulic oil and escape of fuel. It shall be the user’s responsibility to consult with the fire code official concerning the necessary requirements for such protection. | (N)3006.2 Fixed fire-extinguishing systems. Fixed fire-extinguishing systems shall be maintained in accordance with the applicable building code. |  |  | 3006.2 Fixed fire-extinguishing systems. Fixed fire-extinguishing systems shall be maintained in accordance with chapter 9 for Class C or D ovens to protect against such hazards as overheating, spillage of molten salts or metals, quench tanks, ignition of hydraulic oil and escape of fuel.

## Ch31
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
3101.1 Scope. Tents and membrane structures shall comply with this chapter. The provisions of Section 3103 are applicable only to temporary tents and membrane structures. The provisions of Section 3104 are applicable to temporary and permanent tents and membrane structures. | 3101.1 Scope. Tents, temporary stage canopies, and membrane structures shall comply with this chapter. The provisions of Section 3103 are applicable only to temporary tents and membrane structures. The provisions of Section 3104 are applicable to temporary and permanent tents and membrane structures. Other temporary structures shall comply with the applicable building code. |  |  | no change
3103.1 General. All temporary tents and membrane structures shall comply with this section. | (N)3103.1 General. Tents and membrane structures used for temporary periods shall comply with this section. Other temporary structures erected for a period of 180 days or less shall comply with the applicable building code. |  |  | 3103.1 General. All temporary tents and membrane structures shall comply with this section.
3103.2 Approval required. Tents and membrane structures having an area in excess of 400 square feet (37 m2) shall not be erected, operated or maintained for any purpose without first obtaining a permit and approval from the fire code official. Exceptions: 1.Tents used exclusively for recreational camping purposes. 2.Tents open on all sides which comply with all of the following: 2.1.Individual tents having a maximum size of 700 square feet (65 m2). 2.2.The aggregate area of multiple tents placed side by side without a fire break clearance of 12 feet (3658 mm), not exceeding 700 square feet (65 m2) total. 2.3.A minimum clearance of 12 feet (3658 mm) to all structures and other tents. | (N)3103.2 Approval required. Tents and membrane structures having an area in excess of 900 square feet (84 m2 ) shall not be erected, operated or maintained for any purpose without first obtaining a permit and approval from the fire code official in accordance with Table 107.2. |  |  | 3103.2 Approval required. Tents and membrane structures having an area in excess of 900 square feet (84 m2 ) shall not be erected, operated or maintained for any purpose without first obtaining a permit and approval from the fire code official in accordance with Table 107.2.Exceptions: 1.Tents used exclusively for recreational camping purposes. 2.Tents open on all sides which comply with all of the following: 2.1.Individual tents having a maximum size of 700 square feet (65 m2). 2.2.The aggregate area of multiple tents placed side by side without a fire break clearance of 12 feet (3658 mm), not exceeding 700 square feet (65 m2) total. 2.3.A minimum clearance of 12 feet (3658 mm) to all structures and other tents.
None | 3103.2.1 Multiple tents. The aggregate area of multiple tents separated by less than 12 feet (3658 mm) shall not exceed 900 square feet unless approved in accordance with Section 3103.2. |  |  | no change
3103.4 Permits. Permits shall be required as set forth in Section 107.2. | 3103.4 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
None | 3103.9.1 Tents and membrane structures exceeding one story. Tents and membrane structures exceeding one story shall be designed and constructed to comply with applicable building code. |  |  | no change
3104.1 General. All tents and membrane structures, both temporary and permanent, shall be in accordance with this section. Permanent tents and membrane structures shall also comply with the International Building Code. | 3104.1 General. Tents and membrane structures, both temporary and permanent, shall be in accordance with this section. Permanent tents and membrane structures shall also comply with the applicable building code. |  |  | no change
3104.2 Flame propagation performance treatment. Before a permit is granted, the owner or agent shall file with the fire code official a certificate executed by an approved testing laboratory certifying that the tents and membrane structures and their appurtenances; sidewalls, drops and tarpaulins; floor coverings, bunting and combustible decorative materials and effects, including sawdust when used on floors or passageways, are composed of material meeting the flame propagation performance criteria of NFPA 701 or shall be treated with a flame retardant in an approved manner and meet the flame propagation performance criteria of NFPA 701, and that such flame propagation performance criteria are effective for the period specified by the permit. | 3104.2 Flame propagation performance treatment. Before a permit is granted, the owner or agent shall file a certificate executed by an approved testing laboratory certifying that the tents and membrane structures and their appurtenances; sidewalls, drops and tarpaulins; floor coverings, bunting, and combustible decorative materials and effects, including sawdust where used on floors or passageways, are composed of material meeting the flame propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701 or shall be treated with a flame retardant in an approved manner and meet the flame propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701, and that such flame propagation performance criteria are effective for the period specified by the permit. |  |  | no change
3104.4 Certification. An affidavit or affirmation shall be submitted to the fire code official and a copy retained on the premises on which the tent or air-supported structure is located. The affidavit shall attest to the following information relative to the flame propagation performance criteria of the fabric: 1.Names and address of the owners of the tent or air-supported structure. 2.Date the fabric was last treated with flame-retardant solution. 3.Trade name or kind of chemical used in treatment. 4.Name of person or firm treating the material. 5.Name of testing agency and test standard by which the fabric was tested. | 3104.4 Certification. An affidavit or affirmation shall be submitted and a copy retained on the premises on which the tent or air-supported structure is located. The affidavit shall attest to all of the following information relative to the flame propagation performance criteria of the fabric 1. Names and address of the owners of the tent or air-supported structure. 2. Date the fabric was last treated with flame-retardant solution. 3. Trade name or kind of chemical used in treatment. 4. Name of person or firm treating the material. 5. Name of testing agency and test standard by which the fabric was tested. |  | only change was to add back "fire code official" | 3104.4 Certification. An affidavit or affirmation shall be submitted to the fire code official and a copy retained on the premises on which the tent or air-supported structure is located. The affidavit shall attest to the following information relative to the flame propagation performance criteria of the fabric: 1.Names and address of the owners of the tent or air-supported structure. 2.Date the fabric was last treated with flame-retardant solution. 3.Trade name or kind of chemical used in treatment. 4.Name of person or firm treating the material. 5.Name of testing agency and test standard by which the fabric was tested.
3104.13 Fire protection equipment. Fire hose lines, water supplies and other auxiliary fire equipment shall be maintained at the site in such numbers and sizes as required by the fire code official. | 3104.13 Fire protection equipment. Fire hose lines, water supplies, and other auxiliary fire equipment shall be maintained at the site in such numbers and sizes as approved |  |  | Fire hose lines, water supplies and other auxiliary fire equipment shall be maintained at the site in such numbers and sizes as required by the fire code official.
3104.14 Occupant load factors. The occupant load allowed in an assembly structure, or portion thereof, shall be determined in accordance with Chapter 10. | 3104.14 Occupant load factors. The occupant load allowed in an assembly structure, or portion thereof, shall be determined in accordance with Chapter 10 or applicable building code. |  |  | 3104.14 Occupant load factors. The occupant load allowed in an assembly structure, or portion thereof, shall be determined in accordance with Chapter 10.
3104.15.1 Installation. Heating or cooking equipment, tanks, piping, hoses, fittings, valves, tubing and other related components shall be installed as specified in the International Mechanical Code and the International Fuel Gas Code, and shall be approved by the fire code official. | 3104.15.1 Installation. Heating or cooking equipment tanks, piping, hoses, fittings, valves, tubing, and other related components shall be installed as specified by the applicable building code and shall be approved. |  |  | 3104.15.1 Installation. Heating and cooking equipment, tanks, piping, hoses,fittings, valves, tubing and other related componenets shall be operated in accordance with manufacturer specificaitons and other provisions of the this code. Such items shall be maintained in accordance with this code.
3104.15.2 Venting. Gas, liquid and solid fuel-burning equipment designed to be vented shall be vented to the outside air as specified in the International Fuel Gas Code and the International Mechanical Code. Such vents shall be equipped with approved spark arresters when required. Where vents or flues are used, all portions of the tent or membrane structure shall be not less than 12 inches (305 mm) from the flue or vent. | 3104.15.2 Venting. Gas, liquid and solid fuel-burning equipment designed to be vented shall be vented to the outside air as specified by the applicable building code and shall be approved. Such vents shall be equipped with approved spark arresters where required. Where vents or flues are used, all portions of the tent or membrane structure shall be not less than 12 inches (305 mm) from the flue or vent. |  |  | no change
3104.16.1 General. LP-gas equipment such as tanks, piping, hoses, fittings, valves, tubing and other related components shall be approved and in accordance with Chapter 61 and with the International Fuel Gas Code. | 3104.16.1 General. LP-gas equipment such as tanks, piping, hoses, fittings, valves, tubing and other related components shall be approved and in accordance with Chapter 61 and with the applicable building code. |  |  | no change
None | (N)3105.1 General. Operation and maintenance of temporary stage canopies shall be in accordance with Section 3104, Sections 3105.2 through 3105.8, and ANSI E1.21. |  |  | no change
None | (N)3105.2 Approval. Temporary stage canopies in excess of 400 square feet (37 m2 ) shall not be erected for any purpose without first obtaining approval and a permit from the building official. |  | why is this BO only for temp and the opeaton and maintenance. The BO isnt invovled in those aspects. | 3105.2 Approval. Temporary stage canopies in excess of 400 square feet (37 m2 ) shall not be erected for any purpose without first obtaining approval and a permit from the fire official and the building official.
None | (N)3105.5 Required documents. Documents shall be submitted to the building official where required by the USBC. |  |  | 3105.5 Required documents. The following documents shall be submitted to the fire official before apermit is apporved. 1. Designation of responsible party: The owner of the temporary stage canopy shall designate in writing a person to have responsibility for the temporary stage canopy on the site. The designated person shall have sufficient knowledge of the construction documents, manufacturer’s recommendations and operations plan to make judgments regarding the structure’s safety and to coordinate with the fire code official. 2. Operations plan: The operations plan shall reflect manufacturer’s operational guidelines, procedures for environmental monitoring and actions to be taken under specified conditions consistent with the construction documents.
None | (N)3105.6.2 Inspection report. The inspecting agency or individual shall furnish an inspection report to the building official and fire code official. The inspection report shall indicate that the temporary stage canopy was inspected and was or was not installed in accordance with the approved construction documents. Discrepancies shall be brought to the immediate attention of the installer for correction. Where any discrepancy is not corrected, it shall be brought to the attention of the building official and fire code official and the designated responsible party |  |  | no change
None | (N)3105.7 Means of egress. The means of egress for temporary stage canopies shall comply with Chapter 10 and the applicable building code. |  | temporary stage canopies are not historic structures | 3105.7 Means of egress. The means of egress for temporary stage canopies shall comply with Chapter 10.
None | (N)3105.8 Location. (Section deleted) |  |  | 3105.8 Location. Temporary stage canopies shall be located a distance from property lines and buildings to accommodate guy wires, cross-bracing, ground anchors or ballast. Location shall not interfere with egress from a building or encroach on fire apparatus access roads in accordance with this code.

## Ch32
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
3201.1 Scope. High-piled combustible storage shall be in accordance with this chapter. In addition to the requirements of this chapter, the following material-specific requirements shall apply: 1.Aerosols shall be in accordance with Chapter 51. 2.Flammable and combustible liquids shall be in accordance with Chapter 57. 3.Hazardous materials shall be in accordance with Chapter 50. 4.Storage of combustible paper records shall be in accordance with NFPA 13. 5.Storage of combustible fibers shall be in accordance with Chapter 52. 6.General storage of combustible material shall be in accordance with Chapter 3. | (N)3201.1 Scope. Maintenance and operational aspects of high-piled combustible storage shall be in accordance with this chapter. In addition to the requirements of this chapter, the following material-specific requirements shall apply: 1. Aerosols shall be in accordance with Chapter 51. 2. Flammable and combustible liquids shall be in accordance with Chapter 57. 3. Hazardous materials shall be in accordance with Chapter 50. 4. Storage of combustible paper records shall be in accordance with the applicable NFPA 13 standard. 5. Storage of combustible fibers shall be in accordance with Chapter 37. 6. General storage of combustible material shall be in accordance with Chapter 3. |  |  | no change
3201.2 Permits. A permit shall be required as set forth in Section 107.2. | 3201.2 Permits. A permit shall be required as set forth in Section 107.2. |  |  | no change
3201.3 Construction documents. At the time of building permit application for new structures designed to accommodate high-piled storage or for requesting a change of occupancy/use, and at the time of application for a storage permit, plans and specifications shall be submitted for review and approval. In addition to the information required by the International Building Code, the storage permit submittal shall include the information specified in this section. Following approval of the plans, a copy of the approved plans shall be maintained on the premises in an approved location. The plans shall include the following: 1.Floor plan of the building showing locations and dimensions of high-piled storage areas. 2.Usable storage height for each storage area. 3.Number of tiers within each rack, if applicable. 4.Commodity clearance between top of storage and the sprinkler deflector for each storage arrangement. 5.Aisle dimensions between each storage array. 6.Maximum pile volume for each storage array. 7.Location and classification of commodities in accordance with Section 3203. 8.Location of commodities which are banded or encapsulated. 9.Location of required fire department access doors. 10.Type of fire suppression and fire detection systems. 11.Location of valves controlling the water supply of ceiling and in-rack sprinklers. 12.Type, location and specifications of smoke removal and curtain board systems. 13.Dimension and location of transverse and longitudinal flue spaces. 14.Additional information regarding required design features, commodities, storage arrangement and fire protection features within the high-piled storage area shall be provided at the time of permit, when required by the fire code official. | (N)3201.3 Construction documents. (Section deleted) |  |  | 3201.3 High-piled storage operational plan. Prior to the use and operation of high-piled storage in new structures or buildings requesting a change of occupancy/use, plans and specifications shall be submitted to the building official for review and approval. Following approval of the plans, a copy of the approved plans shall be maintained on the premises in an approved location. The on-site plans shall include the following applicable items: 1.Floor plan of the building showing locations and dimensions of high-piled storage areas. 2.Usable storage height for each storage area. 3.Number of tiers within each rack, if applicable. 4.Commodity clearance between top of storage and the sprinkler deflector for each storage arrangement. 5.Aisle dimensions between each storage array. 6.Maximum pile volume for each storage array. 7.Location and classification of commodities in accordance with Section 3203 or the applicable building code. 8.Location of commodities which are banded or encapsulated. 9.Location of required fire department access doors. 10.Type of fire suppression and fire detection systems. 11.Location of valves controlling the water supply of ceiling and in-rack sprinklers. 12.Type, location and specifications of smoke removal and curtain board systems. 13.Dimension and location of transverse and longitudinal flue spaces. 14.Additional information regarding required design features, commodities, storage arrangement and fire protection features within the high-piled storage area when required by the fire code official.
3204.1 General. High-piled storage areas, and portions of high-piled storage areas intended for storage of a different commodity class than adjacent areas, shall be designed and specifically designated to contain Class I, Class II, Class III, Class IV or high-hazard commodities. The designation of a high-piled combustible storage area, or portion thereof intended for storage of a different commodity class, shall be based on the highest hazard commodity class stored except as provided in Section 3204.2. | (N)3204.1 General. The operational and maintenance of high-piled storage areas, and portions of high-piled storage areas intended for storage, shall be maintained in accordance with the applicable building code. |  |  | 3204.1 General. The operation and maintenance of high-piled storage areas, and portions of high-piled storage areas intended for storage, shall be maintained in accordance with the approved plan specfied in section 3201.3 and the applicable building code.
3204.2 Designation based on engineering analysis. The designation of a high-piled combustible storage area, or portion thereof, is allowed to be based on a lower hazard class than that of the highest class of commodity stored when a limited quantity of the higher hazard commodity has been demonstrated by engineering analysis to be adequately protected by the automatic sprinkler system provided. The engineering analysis shall consider the ability of the sprinkler system to deliver the higher density required by the higher hazard commodity. The higher density shall be based on the actual storage height of the pile or rack and the minimum allowable design area for sprinkler operation as set forth in the density/area figures provided in NFPA 13. The contiguous area occupied by the higher hazard commodity shall not exceed 120 square feet (11 m2) and additional areas of higher hazard commodity shall be separated from other such areas by 25 feet (7620 mm) or more. The sprinkler system shall be capable of delivering the higher density over a minimum area of 900 square feet (84 m2) for wet pipe systems and 1,200 square feet (111 m2) for dry pipe systems. The shape of the design area shall be in accordance with Section 903. | (N)3204.2 Designation based on engineering analysis. (Section deleted) |  |  | no change
3206.1 General. Fire protection and life safety features for high-piled storage areas shall be in accordance with Sections 3206.2 through 3206.10. | (N)3206.1 General. Fire protection and life safety features for high-piled storage areas shall be maintained in accordance with the applicable building code. |  |  | 3206.1 General. Fire protection and life safety features for high-piled storage areas shall be maintained in accordance with Sections 3206.2 through 3206.10
3206.2 Extent and type of protection. Where required by Table 3206.2, fire detection systems, smoke and heat removal, draft curtains and automatic sprinkler design densities shall extend the lesser of 15 feet (4572 mm) beyond the high-piled storage area or to a permanent partition. Where portions of high-piled storage areas have different fire protection requirements because of commodity, method of storage or storage height, the fire protection features required by Table 3206.2 within this area shall be based on the most restrictive design requirements. | (N)3206.2 Extent and type of protection. (Section deleted) |  |  | no change
TABLE 3206.2 GENERAL FIRE PROTECTION AND LIFE SAFETY REQUIREMENTS | (N)TABLE 3206.2 GENERAL FIRE PROTECTION AND LIFE SAFETY REQUIREMENTS (Table deleted) |  |  | no change
3206.3 Separation of high-piled storage areas. High-piled storage areas shall be separated from other portions of the building where required by Sections 3206.3.1 through 3206.3.2.2. | (N)3206.3 Separation of high-piled storage areas. (Section deleted) |  |  | 3206.3 Separation of high-piled storage areas. High-piled storage areas shall be maintained as separated from other portions of the building where required by the storage plan in section 3201.3 and the applicable buidling code.
3206.3.1 Separation from other uses. Mixed occupancies shall be separated in accordance with the International Building Code. | (N)3206.3.1 Separation from other uses. (Section deleted) |  |  | 3206.3.1 Separation from other uses. Mixed occupancies shall be maintained as separated in accordance with the storage plan in section 3201.3 and applicable building code.
3206.3.2 Multiple high-piled storage areas. Multiple high-piled storage areas shall be in accordance with Section 3206.3.2.1 or 3206.3.2.2. | (N)3206.3.2 Multiple high-piled storage areas. (Section deleted) |  |  | 3206.3.2 Multiple high-piled storage areas. Multiple high-piled storage areas shall be maintained in accordance with the storage plan in section 3201.3 and the applicable building code.
3206.3.2.1 Aggregate area. The aggregate of all high-piled storage areas within a building shall be used for the application of Table 3206.2 unless such areas are separated from each other by 1-hour fire barriers constructed in accordance with Section 707 the International Building Code. Openings in such fire barriers shall be protected by opening protectives having a 1-hour fire protection rating. | (N)3206.3.2.1 Aggregate area. (Section deleted) |  |  | no change
3206.3.2.2 Multiclass high-piled storage areas. High-piled storage areas classified as Class I through IV not separated from high-piled storage areas classified as high hazard shall utilize the aggregate of all high-piled storage areas as high hazard for the purposes of the application of Table 3206.2. To be considered as separated, 1-hour fire barriers shall be constructed in accordance with Section 707 of the International Building Code. Openings in such fire barriers shall be protected by opening protectives having a 1-hour fire protection rating. Exception: As provided for in Section 3204.2. | (N)3206.3.2.2 Multiclass high-piled storage areas. (Section deleted) |  |  | no change
3206.4 Automatic sprinklers. Automatic sprinkler systems shall be provided in accordance with Sections 3207, 3208 and 3209. | (N)3206.4 Automatic sprinklers. Automatic sprinkler systems shall be maintained in accordance with the applicable building code. |  |  | 3206.4 Automatic sprinklers. Automatic sprinkler systems shall be maintained in accordance with Chapter 9 and remain in accordance with the applicable building code.
None | (N)3206.4.1 Pallets. The requirements based on the presence of pallets shall be maintained in accordance with the applicable building code. |  |  | 3206.4.1 Pallets. The requirements based on the presence of pallets shall be maintained in accordance with the storage plan in section 3201.3 and the applicable building code.
None | (N)3206.4.1.1 Plastic pallets. Plastic pallets listed and labeled in accordance with UL 2335 or FM 4996 shall be treated as wood pallets. |  |  | no change
3206.5 Fire detection. Where fire detection is required by Table 3206.2, an approved automatic fire detection system shall be installed throughout the high-piled storage area. The system shall be monitored and be in accordance with Section 907. | (N)3206.5 Fire detection. Fire detection provided for high-piled storage areas shall be maintained in accordance with the applicable building code. |  |  | 3206.5 Fire detection. Fire detection provided for high-piled storage areas shall be maintained in accordance with Chapter 9 and remain in accordance with the approved storage plan in section 3201.3 and the applicable building code.
3206.6 Building access. Where building access is required by Table 3206.2, fire apparatus access roads in accordance with Section 503 shall be provided within 150 feet (45 720 mm) of all portions of the exterior walls of buildings used for high-piled storage. Exception: Where fire apparatus access roads cannot be installed because of topography, railways, waterways, non-negotiable grades or other similar conditions, the fire code official is authorized to require additional fire protection. | (N)3206.6 Building access. Where building access is required, it shall be maintained in accordance with the applicable building code. |  | Incorporate "Building Access" from table 3206.2 | 3206.6 Building access. Where building access is required by the applicable building code, fire apparatus access roads in accordance with Section 503 shall be provided within 150 feet (45 720 mm) of all portions of the exterior walls of buildings used for high-piled storage. Exception: Where fire apparatus access roads cannot be installed because of topography, railways, waterways, non-negotiable grades or other similar conditions, the fire code official is authorized to require additional fire protection.
3206.6.1 Access doors. Where building access is required by Table 3206.2, fire department access doors shall be provided in accordance with this section. Access doors shall be accessible without the use of a ladder. | (N)3206.6.1 Access doors. Access doors shall be maintained in accordance with the applicable building code. |  |  | 3206.6.1 Access doors. Access doors shall be maintained accessible, available at all times and remain in accordance with the approved storage plan in section 3201.3 and the applicable building code.
3206.6.1.1 Number of doors required. A minimum of one access door shall be provided in each 100 lineal feet (30 480 mm), or fraction thereof, of the exterior walls that face required fire apparatus access roads. The required access doors shall be distributed such that the lineal distance between adjacent access doors does not exceed 100 feet (30 480 mm). | (N)3206.6.1.1 Number of doors required. The minimum number of doors shall be maintained in accordance with the applicable building code. |  |  | 3206.6.1.1 Number of doors required. The minimum number of doors shall be maintained in accordance with the approved storage plan in section 3201.3 and remain in accordance with the applicable building code..
3206.6.1.2 Door size and type. Access doors shall not be less than 3 feet (914 mm) in width and 6 feet 8 inches (2032 mm) in height. Roll-up doors shall not be used unless approved. | (N)3206.6.1.2 Door size and type. Access doors shall be maintained in accordance with the applicable building code. Roll-up doors shall not be used unless approved. |  |  | 3206.6.1.2 Door size and type. Access doors shall be maintained in accordance with the approved storage plan in section 3201.3 and remain in accordance with the applicable building code.. Roll-up doors shall not be used unless approved.
3206.7 Smoke and heat removal. Where smoke and heat removal are required by Table 3206.2, smoke and heat vents shall be provided in accordance with Section 910. Where draft curtains are required by Table 3206.2, they shall be provided in accordance with Section 910.3.5. | (N)3206.7 Smoke and heat removal. Where smoke and heat removal is required, it shall be maintained in accordance with the applicable building code. |  |  | 3206.7 Smoke and heat removal. Where smoke and heat removal systems including draft curtains are required, they shall be maintained in accordance with Chapter 9, the approved storage plan in section 3201.3 and remain in accordance with the applicable building code.
3206.8 Fire department hose connections. Where exit passageways are required by the International Building Code for egress, a Class I standpipe system shall be provided in accordance with Section 905. | (N)3206.8 Fire department hose connections. Where a standpipe system is required for exit passageways, it shall be maintained in accordance with the applicable building code. |  |  | 3206.8 Fire department hose connections. Where a standpipe system is proivded, it shall be maintained in accordance with Chapter 9 and remain in accodance with the applicable building code.
3206.9 Aisles. Aisles providing access to exits and fire department access doors shall be provided in high-piled storage areas exceeding 500 square feet (46 m2), in accordance with Sections 3206.9.1 through 3206.9.3. Aisles separating storage piles or racks shall comply with NFPA 13. Aisles shall also comply with Chapter 10. | (N)3206.9 Aisles. Aisles separating storage piles or racks shall be maintained in accordance with the applicable building code. |  |  | 3206.9 Aisles. Aisles separating storage piles or racks shall be maintained unobstructed and remain in accordance with the approved storage plan in section 3201.3 and applicable building code.
3206.9.1 Width. Aisle width shall be in accordance with Sections 3206.9.1.1 and 3206.9.1.2. Exceptions: 1.Aisles crossing rack structures or storage piles, which are used only for employee access, shall be a minimum of 24 inches (610 mm) wide. 2.Aisles separating shelves classified as shelf storage shall be a minimum of 30 inches (762 mm) wide. | (N)3206.9.1 Width. Aisle width shall be maintained in accordance with the applicable building code. |  |  | 3206.9.1 Width. Aisle width shall be maintained to the approved storage plan in section 3201.3 and remain in accordance with the applicable building code. Exceptions: 1.Aisles crossing rack structures or storage piles, which are used only for employee access, shall be a minimum of 24 inches (610 mm) wide. 2.Aisles separating shelves classified as shelf storage shall be a minimum of 30 inches (762 mm) wide.
3206.9.1.1 Sprinklered buildings. Aisles in sprinklered buildings shall be a minimum of 44 inches (1118 mm) wide. Aisles shall be a minimum of 96 inches (2438 mm) wide in high-piled storage areas exceeding 2,500 square feet (232 m2) in area, that are accessible to the public and designated to contain high-hazard commodities. Exception: Aisles in high-piled storage areas exceeding 2,500 square feet (232 m2) in area, that are accessible to the public and designated to contain high-hazard commodities, are protected by a sprinkler system designed for multiple-row racks of high-hazard commodities shall be a minimum of 44 inches (1118 mm) wide. Aisles shall be a minimum of 96 inches (2438 mm) wide in areas accessible to the public where mechanical stocking methods are used. | (N)3206.9.1.1 Sprinklered buildings. Aisles in sprinklered buildings shall be maintained in accordance with the applicable building code. |  |  | delete
3206.9.1.2 Nonsprinklered buildings. Aisles in nonsprinklered buildings shall be a minimum of 96 inches (2438 mm) wide. | (N)3206.9.1.2 Nonsprinklered buildings. Aisles in nonsprinklered buildings shall be maintained in accordance with the applicable building code. |  |  | delete
3206.9.2 Clear height. The required aisle width shall extend from floor to ceiling. Rack structural supports and catwalks are allowed to cross aisles at a minimum height of 6 feet 8 inches (2032 mm) above the finished floor level, provided that such supports do not interfere with fire department hose stream trajectory. | (N)3206.9.2 Clear height. The required aisle width shall be maintained in accordance with the applicable building code. Rack structural supports and catwalks are allowed to cross aisles at a minimum height of 6 feet 8 inches (2032 mm) above the finished floor level, provided that such supports do not interfere with fire department hose stream trajectory. |  |  | 3206.9.2 Clear height. The required aisle width shall be maintained from the floor to ceiling in accordance with the approved storage plan in Section 3201.3 and applicable building code. Rack structural supports and catwalks are allowed to cross aisles at a minimum height of 6 feet 8 inches (2032 mm) above the finished floor level, provided that such supports do not interfere with fire department hose stream trajectory.
3206.9.3 Dead ends. Dead-end aisles shall be in accordance with Chapter 10. | (N)3206.9.3 Dead-end aisles. (Section deleted) |  |  | 3206.9.3 Dead ends. Dead-end aisles shall not exceed the approved storage plan in section 3201.3.
3207.2 Fire protection. Where automatic sprinklers are required by Table 3206.2, an approved automatic sprinkler system shall be installed throughout the building or to 1-hour fire barriers constructed in accordance with Section 707 of the International Building Code. Openings in such fire barriers shall be protected by opening protectives having a 1-hour fire protection rating. The design and installation of the automatic sprinkler system and other applicable fire protection shall be in accordance with the International Building Code and NFPA 13. | (N)3207.2 Fire protection. Where automatic sprinklers are provided, they shall be maintained in accordance with the applicable building code. |  | duplicate of 3206 | delete
3207.2.1 Shelf storage. Shelf storage greater than 12 feet (3658 mm) but less than 15 feet (4572 mm) in height shall be in accordance with the fire protection requirements set forth in NFPA 13. Shelf storage 15 feet (4572 mm) or more in height shall be protected in an approved manner with special fire protection, such as in-rack sprinklers. | (N)3207.2.1 Shelf storage. Shelf storage greater than 12 feet (3658 mm) but less than 15 feet (4572 mm) in height shall be in accordance with the fire protection requirements set forth in the applicable building code. Shelf storage 15 feet (4572 mm) or more in height shall be protected in an approved manner as required by this code and the applicable building code. |  |  | delete
3207.3 Pile dimension and height limitations. Pile dimensions, the maximum permissible storage height and pile volume shall be in accordance with Table 3206.2. | (N)3207.3 Pile dimension and height limitations. Pile dimensions, the maximum permissible storage height and pile volume shall be in accordance with the applicable building code. |  |  | 3207.3 Pile dimension and height limitations. Pile dimensions, the maximum permissible storage height and pile volume shall be maintained in accordance with the approved storage plan in section 3201.3 and remain in accordance with the applicable building code.
3207.4 Array. Where an automatic sprinkler system design utilizes protection based on a closed array, array clearances shall be provided and maintained as specified by the standard used. | (N)3207.4 Array. Where an automatic sprinkler system design utilizes protection based on a closed array, array clearances shall be maintained as specified by the standard used. |  |  | 3207.4 Array. Where an automatic sprinkler system design utilizes protection based on a closed array, array clearances shall be maintained as specified by the standard used and approved storage plan in section 3201.3.
3208.2 Fire protection. Where automatic sprinklers are required by Table 3206.2, an approved automatic sprinkler system shall be installed throughout the building or to 1-hour fire barriers constructed in accordance with Section 707 of the International Building Code. Openings in such fire barriers shall be protected by opening protectives having a 1-hour fire protection rating. The design and installation of the automatic sprinkler system and other applicable fire protection shall be in accordance with Section 903.3.1.1 and the International Building Code. | (N)3208.2 Fire protection. Where automatic sprinklers are provided, they shall be maintained in accordance with the applicable building code. |  | duplicate of 3206 | (N)3208.2 Fire protection. Where automatic sprinklers are provided, they shall be maintained in accordance with chapter 9.
3208.2.2 Racks with solid shelving. Racks with solid shelving having an area greater than 32 square feet (3 m2), measured between approved flue spaces at all four edges of the shelf, shall be in accordance with this section. Exceptions: 1.Racks with mesh, grated, slatted or similar shelves having uniform openings not more than 6 inches (152 mm) apart, comprised of at least 50 percent of the overall shelf area, and with approved flue spaces are allowed to be treated as racks without solid shelves. 2.Racks used for the storage of combustible paper records, with solid shelving, shall be in accordance with NFPA 13. | (N)3208.2.2 Racks with solid shelving. Racks with solid shelving having an area greater than 20 square feet (1.9 m2 ), measured between approved flue spaces at all four edges of the shelf, shall be in accordance with this section. Exceptions: 1. Racks with mesh, grated, slatted or similar shelves having uniform openings not more than 6 inches (152 mm) apart, comprising not less than 50% of the overall shelf area, and with approved flue spaces are allowed to be treated as racks without solid shelves. 2. Racks used for the storage of combustible paper records with solid shelving shall be in accordance with the applicable building code. |  |  | 3208.2.2 Racks with solid shelving. Racks with solid shelving having an area greater than 20 square feet (1.9 m2 ), measured between approved flue spaces at all four edges of the shelf, shall be maintained in accordance with this section. Exceptions: 1. Racks with mesh, grated, slatted or similar shelves having uniform openings not more than 6 inches (152 mm) apart, comprising not less than 50% of the overall shelf area, and with approved flue spaces are allowed to be treated as racks without solid shelves. 2. Racks used for the storage of combustible paper records with solid shelving shall be in accordance with the applicable NFPA 13 standard.
3208.2.2.1 Fire protection. Fire protection for racks with solid shelving shall be in accordance with NFPA 13. | (N)3208.2.2.1 Fire protection. Fire protection for racks with solid shelving shall be in accordance with the applicable building code. |  | duplicate of 3206 | delete
3208.3 Flue spaces. Flue spaces shall be provided in accordance with Table 3208.3. Required flue spaces shall be maintained. | (N)3208.3 Flue spaces. (Section deleted) |  |  | 3208.3 Flue spaces. Flue spaces shall be maintained in accordance with table 2308.3 or the approved storage plan in section 3201.3 and remain in accordance with the applicable building code.
TABLE 3208.3 REQUIRED FLUE SPACES FOR RACK STORAGE | (N)TABLE 3208.3 REQUIRED FLUE SPACES FOR RACK STORAGE (Table deleted) |  |  | TABLE 3208.3 REQUIRED FLUE SPACES FOR RACK STORAGE
3208.3.1 Flue space protection. Where required by the fire code official, flue spaces required by Table 3208.3, in single-, double- or multiple-row rack storage installations shall be equipped with approved devices to protect the required flue spaces. Such devices shall not be removed or modified. | (N)3208.3.1 Flue space protection. Where required by the fire code official, flue spaces required by the applicable building code, in single-row, double-row, or multiple-row rack storage installations shall be equipped with approved devices to protect the required flue spaces. Such devices shall not be removed or modified. |  |  | 3208.3.1 Flue space protection. Where required by the fire code official, required flue spaces in single-row, double-row, or multiple-row rack storage installations shall be equipped with approved devices to protect the required flue spaces. Such devices shall not be removed or modified.
3208.4 Column protection. Steel building columns shall be protected in accordance with NFPA 13. | (N)3208.4 Column protection. Protection for steel building columns shall be maintained in accordance with the applicable building code. |  |  | 3208.4 Column protection. Fire protection for steel building columns shall be maintained in accordance with approved storage plan in section 3201.3, Chapter 9 and remain in accordance with the applicable building code.
3208.5 Extra-high-rack storage systems. Approval of the fire code official shall be obtained prior to installing extra-high-rack combustible storage. | (N)3208.5 Extra-high-rack storage systems. Approval shall be obtained prior to installing extra high rack combustible storage. |  |  | no change
3208.5.1 Fire protection. Buildings with extra-high-rack combustible storage shall be protected with a specially engineered automatic sprinkler system. Extra-high-rack combustible storage shall be provided with additional special fire protection, such as separation from other buildings and additional built-in fire protection features and fire department access, when required by the fire code official. | (N)3208.5.1 Fire protection. Fire protection provided for buildings with extra high rack combustible storage shall be maintained in accordance with the applicable building code. |  |  | delete
3209.2 Automatic sprinklers. Where automatic sprinklers are required by Table 3206.2, the building shall be equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1. | (N)3209.2 Automatic sprinklers. Where automatic sprinklers are provided, they shall be maintained in accordance with the applicable building code. |  |  | delete
3209.3 Carousel storage. High-piled storage areas having greater than 500 square feet (46 m2) of carousel storage shall be provided with automatic shutdown in accordance with one of the following: 1.An automatic smoke detection system installed in accordance with Section 907, with coverage extending 15 feet (4575 mm) in all directions beyond unenclosed carousel storage systems and which sounds a local alarm at the operator’s station and stops the carousel storage system upon the activation of a single detector. 2.An automatic smoke detection system installed in accordance with Section 907 and within enclosed carousel storage systems, which sounds a local alarm at the operator’s station and stops the carousel storage system upon the activation of a single detector. 3.A single dead-man-type control switch that allows the operation of the carousel storage system only when the operator is present. The switch shall be in the same room as the carousel storage system and located to provide for observation of the carousel system. | (N)3209.3 Carousel storage. High-piled storage areas having greater than 500 square feet (46 m2 ) of carousel storage shall be maintained in accordance with the applicable building code. |  |  | 3209.3 Carousel storage. High-piled storage areas having greater than 500 square feet (46 m2 ) of carousel storage, including automatic shutdown devices, shall be maintained in accordance with the approved storage plan in section 3201.3 and remain in accordance with the applicable building code.
3209.4 Automated rack storage. High-piled storage areas with automated rack storage shall be provided with a manually activated emergency shutdown switch for use by emergency personnel. The switch shall be clearly identified and shall be in a location approved by the fire chief. | (N)3209.4 Automated rack storage. Highpiled storage areas with automated rack storage shall be maintained in accordance with the applicable building code. The switch shall be clearly identified and shall be in a location approved. |  |  | 3209.4 Automated rack storage. High-piled storage areas with automated rack storage shall be maintained in accordance with the approved storage plan in section 3201.3. A manually activated emergency shutdown switch for use by emergency personnel shall be clearly identified and shall be maintained in a location approved by the fire code official.
3210.1 General. Records storage facilities used for the rack or shelf storage of combustible paper records greater than 12 feet (3658 mm) in height shall be in accordance with Sections 3206 and 3208 and NFPA 13. Palletized storage of records shall be in accordance with Section 3207. | (N)3210.1 General. Records storage facilities used for the rack or shelf storage of combustible paper records shall be in accordance with the applicable building code. Palletized storage of records shall be in accordance with the applicable building code. |  |  | 3210.1 General. Records storage facilities used for the rack or shelf storage of combustible paper records greater than 12 feet (3658 mm) in height shall be maintained in accordance with Section 3206 and 3208, the approved storage plan in section 3201.3 and remain in accordance with the applicable building code. Palletized storage of records shall maintained in accordance with Section 3207.

## Ch33
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
3314.1 Completion before occupancy. In buildings where an automatic sprinkler system is required by this code or the International Building Code, it shall be unlawful to occupy any portion of a building or structure until the automatic sprinkler system installation has been tested and approved, except as provided in Section 105.3.4. | 3314.1 Completion before occupancy. In buildings where an automatic sprinkler system is required by this code or the applicable building code, it shall be unlawful to occupy any portion of a building or structure until the automatic sprinkler system installation has been tested and approved, except as provided in Section 106. |  | 109.2 or 110.4 or 901.7 or 901.5.1 | 3314.1 Completion before occupancy. In buildings where an automatic sprinkler system is required by this code or the applicable building code, it shall be unlawful to occupy any portion of a building or structure until the automatic sprinkler system installation has been tested and approved, except as provided in Section 109.2

## Ch34 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
3401.1 Scope. Tire rebuilding plants, tire storage and tire byproduct facilities shall comply with this chapter, other applicable requirements of this code and NFPA 13. Tire storage in buildings shall also comply with Chapter 32. | 3401.1 Scope. The maintenance and operation of tire rebuilding plants, tire storage, and tire byproduct facilities shall comply with this chapter, other applicable requirements of this code, and NFPA 13, as originally approved. Tire storage in buildings shall also comply with Chapter 32. |  |  | 3401.1 Scope. The maintenance and operation of tire rebuilding plants, tire storage, and tire byproduct facilities shall comply with this chapter, other applicable requirements of this code. Tire storage in buildings shall also comply with Chapter 32.
3401.2 Permits. A permit shall be required as set forth in Section 107.2. | 3401.2 Permit required. Permits shall be required as set forth in Section 107.2. |  |  | no change
3403.1 Construction. Tire rebuilding plants shall comply with the requirements of the International Building Code, as to construction, separation from other buildings or other portions of the same building, and protection. | (N)3403.1 Construction. Tire rebuilding plants shall comply with the requirements of the applicable building code. |  |  | 3403.1 Construction. Tire rebuilding plants shall maintain the requirements of the applicable building code, as to construction, separation from other buildings or other portions of the same building, and protection.
3403.2 Location. Buffing operations shall be located in a room separated from the remainder of the building housing the tire rebuilding or tire recapping operations by a 1-hour fire barrier. Exception: Buffing operations are not required to be separated where all of the following conditions are met: 1.Buffing operations are equipped with an approved continuous automatic water-spray system directed at the point of cutting action; 2.Buffing machines are connected to particle-collecting systems providing a minimum air movement of 1,500 cubic feet per minute (cfm) (0.71 m3/s) in volume and 4,500 feet per minute (fpm) (23 m/s) in-line velocity; and 3.The collecting system shall discharge the rubber particles to an approved outdoor noncombustible or fire-resistant container, which is emptied at frequent intervals to prevent overflow. | (N)3403.2 Location. (Section deleted) |  |  | 3403.2 Location. Unless otherwise approved by the applicable building code, buffing operations shall be located in a room separated from the remainder of the building housing the tire rebuilding or tire recapping operations by a fire-resistance rated separation in accordance with the applicable building code. Exception: Where permitted by the applicable building code, buffing operations are not required to be separated where all of the following conditions are met: 1.Buffing operations are equipped with an approved continuous automatic water-spray system directed at the point of cutting action; 2.Buffing machines are connected to particle-collecting systems providing a minimum air movement of 1,500 cubic feet per minute (cfm) (0.71 m3/s) in volume and 4,500 feet per minute (fpm) (23 m/s) in-line velocity; and 3.The collecting system shall discharge the rubber particles to an approved outdoor noncombustible or fire-resistant container, which is emptied at frequent intervals to prevent overflow.
3406.1 Required access. New and existing tire storage yards shall be provided with fire apparatus access roads in accordance with Section 503 and Section 3406.2. | 3406.1 Required access. New and existing tire storage yards shall be provided with fire apparatus access roads in accordance with Section 503 and Section 3406.2. |  |  | no change

## Ch35
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
3501.2 Permits. Permits shall be required as set forth in Section 105.6. | 3501.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change

## Ch36
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
3603.5 Electrical equipment. Electrical equipment shall be installed and used in accordance with its listing, Section 605 of this code and Chapter 5 of NFPA 303 as required for wet, damp and hazardous locations. | (N)3603.5 Electrical equipment. Electrical equipment shall be maintained in accordance with its listing, Section 605 of this code, and NFPA 303 as required for wet, damp, and hazardous locations. |  |  | no change
3604.2 Standpipes. Marinas and boatyards shall be equipped throughout with standpipe systems in accordance with NFPA 303. Systems shall be provided with hose connections located such that no point on the marina pier or float system exceeds 150 feet (15 240 mm) from a standpipe hose connection. | (N)3604.2 Standpipes. Standpipes provided for marinas and boatyards shall be maintained in accordance with the applicable building code. |  | checking consistency of language "of this code" | 3604.2 Standpipes. Marinas and boatyards equipped with standpipe systems shall be maintained in accordance with NFPA 303 and Chapter 9.

## Ch37
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote | Other Comments or Recomendations
None | 3701.3 Permits. Permits shall be required as set forth in Section 107.2. |  |  | No change
None | (N)3703.5 Dust collection. Dust collection and exhaust systems required or provided for equipment or machinery that generates or emits combustible fibers shall be maintained in accordance with the applicable building code. |  | Chapter 22 has combustible dust issues addressed. Combustible dusts and combustible fibers are different materials by definition. If the Chapter 22 wording is not included it appears combustible dusts are not addressed. | 3703.5 Dust collection. Where located within a building, equipment or machinery that generates or emits combustible fibers shall be operated with an approved dust-collecting and exhaust system in accordance with the applicable building code and maintained in accordance with Chapter 22.
None | (N)3704.3 Storage of more than 100 cubic feet to 500 cubic feet. Loose combustible fibers in quantities exceeding 100 cubic feet (3 m3 ) but not exceeding 500 cubic feet (14 m3 ) shall be stored in rooms in accordance with the applicable building code. |  | added "fire reistance rated or other approved" | 3704.3 Storage of more than 100 cubic feet to 500 cubic feet. Loose combustible fibers in quantities exceeding 100 cubic feet (3 m3 ) but not exceeding 500 cubic feet (14 m3 ) shall be stored in rooms in accordance with the applicable building code. These rooms may be required to be fire resistance rated in accordance with the applicable building code. |  | 3704.3 Storage of more than 100 cubic feet to 500 cubic feet. Loose combustible fibers in quantities exceeding 100 cubic feet (3 m3 ) but not exceeding 500 cubic feet (14 m3 ) shall be stored in rooms in accordance with the applicable building code. These rooms may be required to be fire resistance rated in accordance with the applicable building code.
None | (N)3704.4 Storage of more than 500 cubic feet to 1,000 cubic feet. Loose combustible fibers in quantities exceeding 500 cubic feet (14 m3 ) but not exceeding 1,000 cubic feet (28 m3 ) shall be stored in rooms in accordance with the applicable building code. |  | added "fire reistance rated or other approved" | 3704.4 Storage of more than 500 cubic feet to 1,000 cubic feet. Loose combustible fibers in quantities exceeding 500 cubic feet (14 m3 ) but not exceeding 1,000 cubic feet (28 m3 ) shall be stored in rooms in accordance with the applicable building code. These rooms may be required to be fire resistance rated in accordance with the applicable building code. |  | Is there a pointer in the construction code to the IFC provisions
None | (N)3704.5 Storage of more than 1,000 cubic feet. Loose combustible fibers in quantities exceeding 1,000 cubic feet (28 m3 ) shall be stored in rooms in accordance with the applicable building code. |  | added "fire reistance rated or other approved" | 3704.5 Storage of more than 1,000 cubic feet. Loose combustible fibers in quantities exceeding 1,000 cubic feet (28 m3 ) shall be stored in rooms in accordance with the applicable building code. These rooms may be required to be fire resistance rated in accordance with the applicable building code.

## Ch50 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
5001.3.3.9 Reliable power source. Where a power supply is relied upon to prevent or control an emergency condition that could endanger people or property, the power supply shall be from a reliable source. | (N)5001.3.3.9 Reliable power source. Where a power supply is relied upon to prevent or control an emergency condition that could endanger people or property, the power supply shall be maintained in accordance with the applicable building code. |  | Is section 5001.3 a design/construction section? | 5001.3.3.9 Reliable power source. Where a power supply is relied upon to prevent or control an emergency condition that could endanger people or property, the power supply shall be maintained as approved in acordance with the applicable building code.
5001.3.3.10 Ventilation. Where ventilation is necessary to limit the risk of creating an emergency condition resulting from normal or abnormal operations, means of ventilation shall be provided. | (N)5001.3.3.10 Ventilation. Where ventilation is required by the applicable building code maintained. |  | Is section 5001.3 a design/construction section?
5001.5 Permits. Permits shall be required as set forth in Section 107.2. | 5001.5 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
The HMMP shall be maintained onsite for use by emergency responders, and shall be updated not less than annually. | Add the following language to the end of Section 5001.5.1 to read: The HMMP shall be maintained onsite for use by emergency responders and shall be updated not less than annually. |  |  | no change
The HMIS shall be maintained onsite or readily available through another means where approved by the fire code official for use by temporary responders, and shall be updated not less than annually. | Add the following language to the end of Section 5001.5.2 to read: The HMIS shall be maintained onsite or readily available through another means where approved by the fire code official for use by temporary responders, and shall be updated not less than annually. |  |  | no change
5001.5.3 Repository container. When an HMMP or HMIS is required, the owner or operator shall provide a repository container (lock box) or other approved means for the storage of items required in Sections 5001.5.1 and 5001.5.2 so as to be readily available to emergency response personnel. 5001.5.3.1 Location and identification. The repository container (lock box) shall be located, installed and identified in an approved manner. 5001.5.3.2 Keying. All repository containers (lock boxes) shall be keyed as required by the fire code official. | 5001.5.3 Repository container. When a HMMP or HMIS is required, the owner or operator shall provide a repository container (lock box) or other approved means for the storage of items required in Sections 5001.5.1 and 5001.5.2 so as to be readily available to emergency response personnel. 5001.5.3.1 Location and identification. The repository container (lock box) shall be located, installed and identified in an approved manner. 5001.5.3.2 Keying. All repository containers (lock boxes) shall be keyed as required by the fire code official. |  |  | no change
None | 5001.7 Operational requirements for Group B teaching and research laboratories. Teaching and research laboratories in Group B educational occupancies above the 12th grade utilizing Section 430 of the USBC, Part I, Construction, or Section 306.1 of the USBC, Part II, Existing Buildings, shall comply with this section and other applicable requirements of this code. In the case of conflicts between the requirements of Section 430 of the USBC, Part I, Construction, or Section 6 306.1 of the USBC, Part II, Existing Buildings, and provisions of this code other than those set out in this section, Section 430 of the USBC, Part I, Construction, or Section 306.1 of the USBC, Part II, Existing Buildings, as applicable, shall govern. 5001.7.1 Chemical safety reviews. Operating and emergency procedures planning and documentation shall be as set out in Sections 5001.3.3.11 through 5001.3.3.17. Such documentation shall be prepared by laboratory safety personnel or special experts and shall be made available in the workplace for reference and review by employees. Copies of such documentation shall be furnished to the fire code official for review upon request. 5001.7.2 Hazardous materials handling. Receiving, transporting on site, unpacking, and dispensing of hazardous materials shall be carried out by persons trained in proper handling of such materials and shall be performed in accordance with Chapters 50 through 67, as applicable. 5001.7.3 Hazard identification signage. Warning signs for other than building components shall be provided in accordance with Section 5003.5. 5001.7.4 Maintenance of equipment, machinery, and processes. Maintenance of equipment, machinery, and processes used with hazardous materials shall comply with Section 5003.2.6. 5001.7.5 Time sensitive materials. Containers of materials that have the potential to become hazardous during prolonged storage shall be dated when first opened and shall be managed in accordance with NFPA 45, Section 8.2.4.4.1. 5001.7.6 Maintenance of storage, dispensing, use, and handling requirements. Storage, dispensing, use, and handling requirements in the USBC, Part I, Construction, or the USBC, Part II, Existing Buildings, shall be maintained. Operational requirements not affecting the manner of construction shall comply with this chapter and Chapters 51 through 67, as applicable. 5001.7.7 Hazardous wastes. Storage, dispensing, use, and handling of hazardous waste shall comply with this chapter and Chapters 51 through 67, as applicable. 5001.7.8 Container size. The maximum container size for all hazardous materials shall be 5.3 gallons (20 L) for liquids, 50 pounds (23 kg) for solids, 100 cubic feet (2.8. m3 ) for health hazard gases per Table 5003.1.1(2), and 500 cubic feet (14 m3 ) for all other gases in accordance with Table 5003.1.1(1). Exception: Hazardous waste collection containers, for other than Class I and Class II flammable liquids, are permitted to exceed 5.3 gallons (20 L) where approved. 5001.7.9 Density. Quantities of Class I, II, and IIIA combustible or flammable liquids in storage and use within control areas or laboratory suites shall not exceed 8 gallons per 100 square feet (30 L/9.3 m2 ) of floor area, with not more than 4 gallons per 100 square feet (15 L/9.3 m2 ) being in use. Quantities of Class I flammable liquids in storage and use shall not exceed 4 gallons per 100 square feet (15 L/9.3 m2 ) of floor area with not more than 2 gallons (7.5 L) being in use. The maximum in use in open systems is limited to 10% of these quantities. Densities shall be reduced by 25% on the 4th-floor through 6th-floor levels above grade plane of the building and 50% above the 6th-floor level. The density is to be reduced to 50% of these values for buildings that are not protected throughout with an approved automatic fire sprinkler system. Regardless of the density, the maximum allowable quantity per control area or laboratory suite shall not be exceeded. Exception: Density limits may be exceeded in designated hazardous waste collection areas or rooms within a control area or laboratory suite, but stored quantities shall not exceed the maximum allowable quantity per laboratory suite or control area. 5001.7.10 Restricted materials in storage. Storage of pyrophorics and Class 4 oxidizers prohibited by Table 5003.1.1(1) in existing buildings not equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 of the USBC, Part I, Construction, shall be allowed within a control area at 25% of the limits in Table 5003.1.1(1) for a building equipped throughout with an automatic sprinkler system, with no additional increases allowed, provided that such materials are stored in accordance with all of the following: 1. Containers shall be completely sealed and stored according to the manufacturer's recommendations. 2. Storage shall be within approved hazardous materials storage cabinets in accordance with Section 5003.8.7 or shall be located in an inert atmosphere glove box in accordance with NFPA 45, Section 7.11. 3. The storage cabinet or glove box shall not contain any storage of incompatible materials. 5001.7.11 Restricted materials in use. Use of pyrophorics and Class 4 oxidizers prohibited by Table 5003.1.1(1) in existing buildings not equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 of the USBC, Part I, Construction, shall be allowed within a control area at 25% of the limits in Table 5003.1.1(1) for buildings equipped throughout with an automatic sprinkler system, with no additional increases allowed, provided that such materials are used in accordance with all of the following: 1. Use shall be within an approved chemical fume hood listed in accordance with UL 1805, or in an inert atmosphere glove box in accordance with NFPA 45, Section 7.11, or other approved equipment designed for the specific hazard of the material. 2. Combustible materials shall be kept at least 2 feet (610 mm) away from the work area, except for those items directly related to the research. 3. A portable fire extinguisher appropriate for the specific material shall be provided within 20 feet (6096 mm) of the use in accordance with Section 906. |  |  | no change
None | Add a new "Permissible fireworks" row to Table 5003.1.1(1) to read: Permissible fireworks 1.4G H-3 125d,e,l NA NA NA NA NA NA NA |  |  | no change
5003.1.3 Quantities not exceeding the maximum allowable quantity per control area. The storage, use and handling of hazardous materials in quantities not exceeding the maximum allowable quantity per control area indicated in Tables 5003.1.1(1) through 5003.1.1(4) shall be in accordance with Sections 5001 and 5003. | (N)5003.1.3 Quantities not exceeding the maximum allowable quantity per control area. (Section deleted) |  |  | 5003.1.3 Quantities not exceeding the maximum allowable quantity per control area. The storage, use and handling of hazardous materials in quantities not exceeding the maximum allowable quantity per control area indicated in Tables 5003.1.1(1) through 5003.1.1(4) shall be in accordance with Sections 5001 and 5003.
5003.1.4 Quantities exceeding the maximum allowable quantity per control area. The storage and use of hazardous materials in quantities exceeding the maximum allowable quantity per control area indicated in Tables 5003.1.1(1) through 5003.1.1(4) shall be in accordance with this chapter. | (N)5003.1.4 Quantities exceeding the maximum allowable quantity per control area. (Section deleted) |  |  | 5003.1.4 Quantities exceeding the maximum allowable quantity per control area. The storage and use of hazardous materials in quantities exceeding the maximum allowable quantity per control area indicated in Tables 5003.1.1(1) through 5003.1.1(4) shall be approved by the Building Code Official in accordance with the applicable building code.
5003.2 Systems, equipment and processes. Systems, equipment and processes utilized for storage, dispensing, use or handling of hazardous materials shall be in accordance with Sections 5003.2.1 through 5003.2.8. | (N)5003.2 Systems, equipment and processes. Systems, equipment and processes utilized for storage, dispensing, use or handling of hazardous materials shall be maintained in accordance with the applicable building code. |  | Look at subsections
5003.2.1 Design and construction of containers, cylinders and tanks. Containers, cylinders and tanks shall be designed and constructed in accordance with approved standards. Containers, cylinders, tanks and other means used for containment of hazardous materials shall be of an approved type. Pressure vessels shall comply with the ASME Boiler and Pressure Vessel Code. | (N)5003.2.1 Design and construction of containers, cylinders and tanks. Portable containers and cylinders shall be designed and constructed in accordance with approved standards. Containers, cylinders, and other means used for containment of hazardous materials shall be of an approved type. Pressure vessels not meeting U.S. Department of Transportation requirements for transportation shall comply with the ASME Boiler and Pressure Vessel Code. Tanks shall be maintained in accordance with the applicable building code. |  |  | (N)5003.2.1 Design and construction of containers, cylinders and tanks. Portable containers and cylinders shall be designed and constructed in accordance with approved standards. Containers, cylinders, and other means used for containment of hazardous materials shall be of an approved type. Pressure vessels not meeting U.S. Department of Transportation requirements for transportation shall comply with the ASME Boiler and Pressure Vessel Code. Tanks shall be maintained as approved in accordance with the applicable building code.
5003.2.2 Piping, tubing, valves and fittings. Piping, tubing, valves, and fittings conveying hazardous materials shall be designed and installed in accordance with ASME B31 or other approved standards, and shall be in accordance with Sections 5003.2.2.1 and 5003.2.2.2. | (N)5003.2.2 Piping, tubing, valves and fittings. Piping, tubing, valves, and fittings conveying hazardous materials shall be maintained in accordance with the applicable building code. |  | There are maintanence requirements in ASME B31 | (N)5003.2.2 Piping, tubing, valves and fittings. Piping, tubing, valves, and fittings conveying hazardous materials shall be maintained as approved in accordance with the applicable building code.
5003.2.2.1 Design and construction. Piping, tubing, valves, fittings and related components used for hazardous materials shall be in accordance with the following: 1.Piping, tubing, valves, fittings and related components shall be designed and fabricated from materials that are compatible with the material to be contained and shall be of adequate strength and durability to withstand the pressure, structural and seismic stress and exposure to which they are subject. 2.Piping and tubing shall be identified in accordance with ASME A13.1 to indicate the material conveyed. 3.Readily accessible manual valves or automatic remotely activated fail-safe emergency shutoff valves shall be installed on supply piping and tubing at the following locations: 3.1.The point of use. 3.2.The tank, cylinder or bulk source. 4.Manual emergency shutoff valves and controls for remotely activated emergency shutoff valves shall be identified and the location shall be clearly visible, accessible and indicated by means of a sign. 5.Backflow prevention or check valves shall be provided when the backflow of hazardous materials could create a hazardous condition or cause the unauthorized discharge of hazardous materials. 6.Where gases or liquids having a hazard ranking of: Health Class 3 or 4 Flammability Class 4 Instability Class 3 or 4 in accordance with NFPA 704 are carried in pressurized piping above 15 pounds per square inch gauge (psig) (103 kPa), an approved means of leak detection and emergency shutoff or excess flow control shall be provided. Where the piping originates from within a hazardous material storage room or area, the excess flow control shall be located within the storage room or area. Where the piping originates from a bulk source, the excess flow control shall be located as close to the bulk source as practical. Exceptions: 1.Piping for inlet connections designed to prevent backflow. 2.Piping for pressure relief devices. | (N)5003.2.2.1 Design and construction. (Section deleted) |  |  | no change
| (N)5003.2.2.2 Additional regulations for supply piping for health-hazard materials. Supply piping and tubing for gases and liquids shall be maintained in accordance with the applicable building code. |  |  | delete
5003.2.3 Equipment, machinery and alarms. Equipment, machinery and required detection and alarm systems associated with the use, storage or handling of hazardous materials shall be listed or approved. | (N)5003.2.3 Equipment, machinery and alarms. Equipment and machinery associated with the use, storage or handling of hazardous materials shall be listed or approved. |  |  | 5003.2.3 Equipment, machinery and alarms. Equipment, machinery and detection and alarm systems associated with the use, storage or handling of hazardous materials shall be listed or approved.
5003.2.4 Installation of tanks. Installation of tanks shall be in accordance with Sections 5003.2.4.1 through 5003.2.4.2.1. | (N)5003.2.4 Installation of tanks. Installation of tanks shall be in accordance with Sections 5003.2.4.1 through 5003.2.4.2.1. |  |  | no change
5003.2.4.1 Underground tanks. Underground tanks used for the storage of liquid hazardous materials shall be provided with secondary containment. In lieu of providing secondary containment for an underground tank, an above-ground tank in an underground vault complying with Section 5704.2.8 shall be permitted. | (N)5003.2.4.1 Underground tanks. Underground tanks used for the storage of liquid hazardous materials shall be maintained in accordance with the applicable building code.
5003.2.4.2 Above-ground tanks. Above-ground stationary tanks used for the storage of hazardous materials shall be located and protected in accordance with the requirements for outdoor storage of the particular material involved. Exception: Above-ground tanks that are installed in vaults complying with Section 5303.16 or 5704.2.8 shall not be required to comply with location and protection requirements for outdoor storage. | (N)5003.2.4.2 Aboveground tanks. Aboveground stationary tanks used for the storage of hazardous materials shall be maintained in accordance with the requirements for outdoor storage of the particular material involved.
5003.2.7 Liquid-level limit control. Atmospheric tanks having a capacity greater than 500 gallons (1893 L) and which contain hazardous material liquids shall be equipped with a liquid-level limit control or other approved means to prevent overfilling of the tank. | (N)5003.2.7 Liquid-level limit control. (Section deleted)
5003.2.8 Seismic protection. Machinery and equipment utilizing hazardous materials shall be braced and anchored in accordance with the seismic design requirements of the International Building Code for the seismic design category in which the machinery or equipment is classified. | (N)5003.2.8. Seismic protection. Where provided, bracing and anchoring for machinery and equipment utilizing hazardous materials shall be maintained in accordance with the applicable building code.
5003.2.9.1 Equipment, devices and systems requiring testing. The following equipment, systems and devices shall be tested in accordance with Sections 5003.2.9 and 5003.2.9.2. 1.Gas detection systems, alarms and automatic emergency shutoff valves required by Section 6004.2.2.10 for highly toxic and toxic gases. 2.Limit control systems for liquid level, temperature and pressure required by Sections 5003.2.7, 5004.8 and 5005.1.4. 3.Emergency alarm systems and supervision required by Sections 5004.9 and 5005.4.4. 4.Monitoring and supervisory systems required by Sections 5004.10 and 5005.1.6. 5.Manually activated shutdown controls required by Section 6403.1.1.1 for compressed gas systems conveying pyrophoric gases. | 5003.2.9.1 Equipment, devices and systems requiring testing. The following equipment, systems, and devices shall be tested in accordance with Sections 5003.2.9 and 5003.2.9.2. 1. Gas detection systems, alarms, and automatic emergency shutoff valves required by Section 6004.2.2.10 for highly toxic and toxic gases. 2. Limit control systems for liquid level, temperature and pressure required by Sections 5004.8 and 5005.1.4. 3. Emergency alarm systems and supervision required by Sections 5004.9 and 5005.4.4. 4. Monitoring and supervisory systems required by the applicable building code. 5. Manually activated shutdown controls required by the applicable building code for compressed gas systems conveying pyrophoric gases.
5003.3.1.4 Responsibility for cleanup. The person, firm or corporation responsible for an unauthorized discharge shall institute and complete all actions necessary to remedy the effects of such unauthorized discharge, whether sudden or gradual, at no cost to the jurisdiction. The fire code official may require records and receipts to verify cleanup and proper disposal of unauthorized discharges. When deemed necessary by the fire code official, cleanup may be initiated by the fire department or by an authorized individual or firm. Costs associated with such cleanup shall be borne by the owner, operator or other person responsible for the unauthorized discharge. | 5003.3.1.4 Responsibility for cleanup. The person, firm, or corporation responsible for an unauthorized discharge shall institute and complete all actions necessary to remedy the effects of such unauthorized discharge, whether sudden or gradual, at no cost to the jurisdiction. The fire code official may require records and receipts to verify cleanup and proper disposal of unauthorized discharges. When deemed necessary by the fire code official, cleanup may be initiated by the fire department or by an authorized individual or firm. Costs associated with such cleanup shall be the responsibility of the owner, operator, or other person responsible for the unauthorized discharge. Note: Owners and operators of certain underground and aboveground petroleum storage tanks may have access to the Virginia Petroleum Storage Tank Fund for reimbursement of some cleanup costs associated with petroleum discharges from these tanks. See Article 10 (§ 62.1-44.34:10 et seq.) of Title 62.1of the Code of Virginia.
5003.8 Construction requirements. Buildings, control areas, enclosures and cabinets for hazardous materials shall be in accordance with Sections 5003.8.1 through 5003.8.6.3. | (N)5003.8 Construction requirements. (Section deleted)
5003.8.1 Buildings. Buildings, or portions thereof, in which hazardous materials are stored, handled or used shall be constructed in accordance with the International Building Code. | (N)5003.8.1 Buildings. Buildings, or portions thereof, in which hazardous materials are stored, handled or used shall be maintained in accordance with the applicable building code.
5003.8.2 Required detached buildings. Group H occupancies containing quantities of hazardous materials in excess of those set forth in Table 5003.8.2 shall be in detached buildings. | (N)5003.8.2 Required detached buildings. (Section deleted)
TABLE 5003.8.2 DETACHED BUILDING REQUIRED | (N)TABLE 5003.8.2 DETACHED BUILDING REQUIRED (Table deleted)
5003.8.3 Control areas. Control areas shall comply with Sections 5003.8.3.1 through 5003.8.3.5. | (N)5003.8.3 Control areas. Control areas shall comply with Sections 5003.8.3.2 through 5003.8.3.4.
5003.8.3.1 Construction requirements. Control areas shall be separated from each other by fire barriers constructed in accordance with Section 707 of the International Building Code or horizontal assemblies constructed in accordance with Section 711 of the International Building Code, or both. | (N)5003.8.3.1 Construction requirements. (Section deleted) |  |  | 5003.8.3.1 Construction requirements. Control areas shall be maintained in accordance with this chapter and the applicable Building Code..
5003.8.3.2 Percentage of maximum allowable quantities. The percentage of maximum allowable quantities of hazardous materials per control area allowed at each floor level within a building shall be in accordance with Table 5003.8.3.2. | (N)5003.8.3.2 Percentage of maximum allowable quantities. The percentage of maximum allowable quantities of hazardous materials per control area allowed at each floor level within a building shall be maintained in accordance with the applicable building code. |  |  | 5003.8.3.2 Percentage of maximum allowable quantities. The percentage of maximum allowable quantities of hazardous materials per control area allowed at each floor level within a building shall be maintained in accordance with this chapter and the applicable building code.
TABLE 5003.8.3.2 DESIGN AND NUMBER OF CONTROL AREAS | (N)TABLE 5003.8.3.2 DESIGN AND NUMBER OF CONTROL AREAS (Table deleted)
5003.8.3.3 Number. The maximum number of control areas per floor within a building shall be in accordance with Table 5003.8.3.2. | (N)5003.8.3.3 Number. The maximum number of control areas per floor within a building shall be maintained in accordance with the applicable building code. |  |  | 5003.8.3.3 Number. The maximum number of control areas per floor within a building shall be maintained in accordance with this chapter and the applicable building code.
5003.8.3.4 Fire-resistance-rating requirements. The required fire-resistance rating for fire barriers shall be in accordance with Table 5003.8.3.2. The floor assembly of the control area and the construction supporting the floor of the control area shall have a fire-resistance rating of not less than 2-hours. Exception: The floor assembly of the control area and the construction supporting the floor of the control area is allowed to be 1-hour fire-resistance rated in buildings of Type IIA, IIIA and VA construction, provided that both of the following conditions exist: 1.The building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1; and 2.The building is three stories or less above grade plane. | (N)5003.8.3.4 Fire-resistance-rating requirements. The required fire-resistance rating for control areas shall be maintained in accordance with the applicable building code. |  |  | 5003.8.3.4 Fire-resistance-rating requirements. The required fire-resistance rating for control areas shall be maintained in accordance with this chapter and the applicable building code.
5003.8.3.5 Hazardous material in Group M display and storage areas and in Group S storage areas. The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials allowed within a single control area of a Group M display and storage area or a Group S storage area is allowed to exceed the maximum allowable quantities per control area specified in Tables 5003.1.1(1) and 5003.1.1(2) without classifying the building or use as a Group H occupancy, provided that the materials are displayed and stored in accordance with Section 5003.11. | (N)5003.8.3.5 Hazardous material in Group M display and storage areas and in Group S storage areas. (Section deleted) |  |  | 5003.8.3.5 Hazardous material in Group M display and storage areas and in Group S storage areas. The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials allowed within a single control area of a Group M display and storage area or a Group S storage area shall comply with this chapter and the applicable building code.The aggregate quantity is allowed to exceed the maximum allowable quantities per control area ,without classifying the building or use as a Group H occupancy, provided that the materials are displayed and stored in accordance with Section 5003.11 and the applicable building code.
5003.8.4 Gas rooms. Where a gas room is provided to comply with the provisions of Chapter 60, the gas room shall be in accordance with Sections 5003.8.4.1 and 5003.8.4.2. | (N)5003.8.4 Gas rooms. (Section deleted) |  |  | 5003.8.4 Gas rooms. Where a gas room is provided it shall me maintained in accordance with the provisions of Chapter 60, this chapter, and the applicable building code.
5003.8.4.1 Construction. Gas rooms shall be protected with an automatic sprinkler system. Gas rooms shall be separated from the remainder of the building in accordance with the requirements of the International Building Code based on the occupancy group into which it has been classified. | (N)5003.8.4.1 Construction. (Section deleted) |  |  | 5003.8.4.1 Construction. Gas rooms shall be maintained, protected and separated from the remainder of the building in accordance with the requirements applicable building code.
5003.8.4.2 Ventilation system. The ventilation system for gas rooms shall be designed to operate at a negative pressure in relation to the surrounding area. Highly toxic and toxic gases shall also comply with Section 6004.2.2.6. The ventilation system shall be installed in accordance with the International Mechanical Code. | (N)5003.8.4.2 Ventilation system. The ventilation system for gas rooms shall be maintained in accordance with the applicable building code. |  |  | 5003.8.4.2 Ventilation system. The ventilation system for gas rooms shall be maintained in accordance with this chapter, Chapter 60, the applicable building code.
5003.8.5 Exhausted enclosures. Where an exhausted enclosure is used to increase maximum allowable quantity per control area or when the location of hazardous materials in exhausted enclosures is provided to comply with the provisions of Chapter 60, the exhausted enclosure shall be in accordance with Sections 5003.8.5.1 through 5003.8.5.3. | (N)5003.8.5 Exhausted enclosures. Where an exhausted enclosure is used to increase maximum allowable quantity per control area, the exhausted enclosure shall be maintained in accordance with the applicable building code |  |  | 5003.8.5 Exhausted enclosures. Where an exhausted enclosure is used to increase maximum allowable quantity per control area, the exhausted enclosure shall be maintained in accordance with this chapter, Chapter 60, and as approved by the applicable building code
5003.8.5.1 Construction. Exhausted enclosures shall be of noncombustible construction. | (N)5003.8.5.1 Construction. (Section deleted) |  |  | 5003.8.5.1 Construction. Exhausted enclosures shall be maintained as approved by the applicable building code..
5003.8.5.2 Ventilation. Exhausted enclosures shall be provided with an exhaust ventilation system. The ventilation system for exhausted enclosures shall be designed to operate at a negative pressure in relation to the surrounding area. Ventilation systems used for highly toxic and toxic gases shall also comply with Items 1, 2 and 3 of Section 6004.1.2. The ventilation system shall be installed in accordance with the International Mechanical Code. | (N)5003.8.5.2 Ventilation. The ventilation system for exhausted enclosures shall be maintained in accordance with the applicable building code. |  |  | 5003.8.5.2 Ventilation. The ventilation system for exhausted enclosures shall be maintained in accordance with this chapter, Chapter 60, and approved by the applicable building code.
5003.8.5.3 Fire-extinguishing system. Exhausted enclosures where flammable materials are used shall be protected by an approved automatic fire-extinguishing system in accordance with Chapter 9. | (N)5003.8.5.3 Fire-extinguishing system. Fire-extinguishing systems required for exhaust enclosures shall be maintained in accordance with the applicable building code. |  |  | 5003.8.5.3 Fire-extinguishing system. Fire-extinguishing systems required for exhaust enclosures shall be maintained in accordance with Chapter 9 and the applicable building code.
5003.8.6.2 Ventilation. Gas cabinets shall be provided with an exhaust ventilation system. The ventilation system for gas cabinets shall be designed to operate at a negative pressure in relation to the surrounding area. Ventilation systems used for highly toxic and toxic gases shall also comply with Items 1, 2 and 3 of Section 6004.1.2. The ventilation system shall be installed in accordance with the International Mechanical Code. | (N)5003.8.6.2 Ventilation. The ventilation system for gas cabinets shall be maintained in accordance with the applicable building code. |  |  | 5003.8.6.2 Ventilation. The ventilation system for exhausted enclosures shall be maintained in accordance with this chapter, Chapter 60, and approved by the applicable building code.
5003.9.9 Shelf storage. Shelving shall be of substantial construction, and shall be braced and anchored in accordance with the seismic design requirements of the International Building Code for the seismic zone in which the material is located. Shelving shall be treated, coated or constructed of materials that are compatible with the hazardous materials stored. Shelves shall be provided with a lip or guard when used for the storage of individual containers. Exceptions: 1.Storage in hazardous material storage cabinets or laboratory furniture specifically designed for such use. 2.Storage of hazardous materials in amounts not requiring a permit in accordance with Section 5001.5. Shelf storage of hazardous materials shall be maintained in an orderly manner. | (N)5003.9.9 Shelf storage. Shelving shall be maintained in accordance with the applicable building code. |  | Shelf storage is not addressed in the building code but is addressed in NFPA 30. Shelves are not a construction item. | 5003.9.9 Shelf storage. Shelving shall be of substantial construction, comply with the requirements of this chapter and NFPA 30, and shall be braced and anchored in accordance with the seismic design requirements of the appicable Building Code. Shelving shall be treated, coated or constructed of materials that are compatible with the hazardous materials stored. Shelves shall be provided with a lip or guard when used for the storage of individual containers. Exceptions: 1.Storage in hazardous material storage cabinets or laboratory furniture specifically designed for such use. 2.Storage of hazardous materials in amounts not requiring a permit in accordance with Section 5001.5. Shelf storage of hazardous materials shall be maintained in an orderly manner.
5003.11 Group M storage and display and Group S storage. The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials stored and displayed within a single control area of a Group M occupancy, or an outdoor control area, or stored in a single control area of a Group S occupancy, is allowed to exceed the maximum allowable quantity per control area indicated in Section 5003.1 when in accordance with Sections 5003.11.1 through 5003.11.3.10. | (N)5003.11 Group M storage and display and Group S storage. The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials stored and displayed within a single control area of a Group M occupancy, or an outdoor control area, or stored in a single control area of a Group S occupancy shall be maintained in accordance with the applicable building code. |  |  | 5003.11 Group M storage and display and Group S storage. The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials stored and displayed within a single control area of a Group M occupancy, or an outdoor control area, or stored in a single control area of a Group S occupancy shall be maintained in accordance this Chapter and the applicable building code.
5003.11.1 Maximum allowable quantity per control area in Group M or S occupancies. The aggregate amount of nonflammable solid and nonflammable or noncombustible liquid hazardous materials stored and displayed within a single control area of a Group M occupancy or stored in a single control area of a Group S occupancy shall not exceed the amounts set forth in Table 5003.11.1. | (N)5003.11.1 Maximum allowable quantity per control area in Group M or S occupancies. The aggregate amount of nonflammable solid and nonflammable or noncombustible liquid hazardous materials stored and displayed within a single control area of a Group M occupancy or stored in a single control area of a Group S occupancy shall not exceed the amounts set forth in the applicable building code. |  |  | 5003.11.1 Maximum allowable quantity per control area in Group M or S occupancies. The aggregate amount of nonflammable solid and nonflammable or noncombustible liquid hazardous materials stored and displayed within a single control area of a Group M occupancy or stored in a single control area of a Group S occupancy shall comply with this Chapter, and not exceed the amounts permissible by the applicable building code.
TABLE 5003.11.1 MAXIMUM ALLOWABLE QUANTITY PER INDOOR AND OUTDOOR CONTROL AREA IN GROUP M AND S OCCUPANCIES—NONFLAMMABLE SOLIDS, NONFLAMMABLE AND NONCOMBUSTIBLE LIQUIDSd, e, f | (N)Table 5003.11.1 MAXIMUM ALLOWABLE QUANTITY PER INDOOR AND OUTDOOR CONTROL AREA IN GROUP M AND S OCCUPANCIES—NONFLAMMABLE SOLIDS, NONFLOMMABLE AND NONCOMBUSTIBLE LIQUIDS (Table deleted)
5003.11.2 Maximum allowable quantity per outdoor control area in Group M or S occupancies. The aggregate amount of nonflammable solid and nonflammable or noncombustible liquid hazardous materials stored and displayed within a single outdoor control area of a Group M occupancy shall not exceed the amounts set forth in Table 5003.11.1. | (N)5003.11.2 Maximum allowable quantity per outdoor control area in Group M or S occupancies. The aggregate amount of nonflammable solid and nonflammable or noncombustible liquid hazardous materials stored and displayed within a single outdoor control area of a Group M occupancy shall not exceed the amounts set forth in the applicable building code. |  |  | 5003.11.2 Maximum allowable quantity per outdoor control area in Group M or S occupancies. The aggregate amount of nonflammable solid and nonflammable or noncombustible liquid hazardous materials stored and displayed within a single outdoor control area of a Group M occupancy shall not exceed the amounts set forth in this Chapter and the applicable building code.
5003.11.3 Storage and display. Storage and display shall be in accordance with Sections 5003.11.3.1 through 5003.11.3.10. | (N)5003.11.3 Storage and display. Storage and display shall be maintained in accordance with the applicable building code. |  |  | 5003.11.3 Storage and display. Storage and display shall be maintained in accordance with this Chapter and the applicable building code.
5003.11.3.1 Density. Storage and display of solids shall not exceed 200 pounds per square foot (976 kg/m2) of floor area actually occupied by solid merchandise. Storage and display of liquids shall not exceed 20 gallons per square foot (0.50 L/m2) of floor area actually occupied by liquid merchandise. | (N)5003.11.3.1 Density. (Section deleted) |  |  | 5003.11.3.1 Density. Storage and display of solids and liquids shall comply with this Chapter and not exceed the limits as approved by the appliable building code.
5003.11.3.2 Storage and display height. Display height shall not exceed 6 feet (1829 mm) above the finished floor in display areas of Group M occupancies. Storage height shall not exceed 8 feet (2438 mm) above the finished floor in storage areas of Group M and Group S occupancies. | (N)5003.11.3.2 Storage and display height. Display height shall not exceed 6 feet (1829 mm) above the finished floor in display areas of Group M occupancies unless approved by the applicable building code. Storage height shall not exceed 8 feet (2438 mm) above the finished floor in storage areas of Group M and Group S occupancies unless approved by the applicable building code. |  | This is an NFPA 13 requirement and also determines when high piled storage requirements are applied. The height of storage is an operational concern not a use concern. | 5003.11.3.2 Storage and display height. Display height shall not exceed 6 feet (1829 mm) above the finished floor in display areas of Group M occupancies. Storage height shall not exceed 8 feet (2438 mm) above the finished floor in storage areas of Group M and Group S occupancies.
5003.11.3.4 Racks and shelves. Racks and shelves used for storage or display shall be in accordance with Section 5003.9.9. | (N)5003.11.3.4 Racks and shelves. Racks and shelves used for storage or display shall be maintained in accordance with the applicable building code. |  |  | 5003.11.3.4 Racks and shelves. Racks and shelves used for storage or display shall be maintained in accordance this chapter and as approved by the applicable building code.
5003.11.3.8 Floors. Floors shall be in accordance with Section 5004.12. | (N)5003.11.3.8 Floors. Floors shall be maintained in accordance with the applicable building code. |  |  | 5003.11.3.8 Floors. Floors shall be maintained in accordance with this Chapter and the applicable building code.
5004.1 Scope. Storage of hazardous materials in amounts exceeding the maximum allowable quantity per control area as set forth in Section 5003.1 shall be in accordance with Sections 5001, 5003 and 5004. Storage of hazardous materials in amounts not exceeding the maximum allowable quantity per control area as set forth in Section 5003.1 shall be in accordance with Sections 5001 and 5003. Retail and wholesale storage and display of nonflammable solid and nonflammable and noncombustible liquid hazardous materials in Group M occupancies and Group S storage shall be in accordance with Section 5003.11. | (N)5004.1 Scope. Storage of hazardous materials shall be maintained in accordance with the applicable building code. Retail and wholesale storage and display of nonflammable solid and nonflammable and noncombustible liquid hazardous materials in Group M occupancies and Group S storage shall be maintained in accordance with the applicable building code. |  |  | 5004.1 Scope. Storage of hazardous materials shall be maintained in accordance with this Chapter and the applicable building code. Retail and wholesale storage and display of nonflammable solid and nonflammable and noncombustible liquid hazardous materials in Group M occupancies and Group S storage shall be maintained in accordance with this Chapter and the applicable building code.
5004.2 Spill control and secondary containment for liquid and solid hazardous materials. Rooms, buildings or areas used for the storage of liquid or solid hazardous materials shall be provided with spill control and secondary containment in accordance with Sections 5004.2.1 through 5004.2.3. Exception: Outdoor storage of containers on approved containment pallets in accordance with Section 5004.2.3. | (N)5004.2 Spill control and secondary containment for liquid and solid hazardous materials. Spill control and secondary containment for rooms, buildings or areas used for the storage of liquid or solid hazardous materials shall be maintained in accordance with the applicable building code. Exception: Outdoor storage of containers on approved containment pallets in accordance with Section 5004.2.3. |  |  | 5004.2 Spill control and secondary containment for liquid and solid hazardous materials. Spill control and secondary containment for rooms, buildings or areas used for the storage of liquid or solid hazardous materials shall be maintained in accordance with the Chapter the applicable building code. Exception: Outdoor storage of containers on approved containment pallets in accordance with Section 5004.2.3.
5004.2.1 Spill control for hazardous material liquids. Rooms, buildings or areas used for the storage of hazardous material liquids in individual vessels having a capacity of more than 55 gallons (208 L), or in which the aggregate capacity of multiple vessels exceeds 1,000 gallons (3785 L), shall be provided with spill control to prevent the flow of liquids to adjoining areas. Floors in indoor locations and similar surfaces in outdoor locations shall be constructed to contain a spill from the largest single vessel by one of the following methods: 1.Liquid-tight sloped or recessed floors in indoor locations or similar areas in outdoor locations. 2.Liquid-tight floors in indoor locations or similar areas in outdoor locations provided with liquid-tight raised or recessed sills or dikes. 3.Sumps and collection systems. 4.Other approved engineered systems. Except for surfacing, the floors, sills, dikes, sumps and collection systems shall be constructed of noncombustible material, and the liquid-tight seal shall be compatible with the material stored. When liquid-tight sills or dikes are provided, they are not required at perimeter openings having an open-grate trench across the opening that connects to an approved collection system. | (N)5004.2.1 Spill control for hazardous material liquids. (Section deleted) |  |  | 5004.2.1 Spill control for hazardous material liquids. Rooms, buildings or areas used for the storage of hazardous material liquids required to be provided with spill control to prevent the flow of liquids to adjoining areas by the applicable building code shall be maintained in accordance with this Chapter and and as approved by applicable building code.
5004.2.2 Secondary containment for hazardous material liquids and solids. Where required by Table 5004.2.2 buildings, rooms or areas used for the storage of hazardous materials liquids or solids shall be provided with secondary containment in accordance with this section when the capacity of an individual vessel or the aggregate capacity of multiple vessels exceeds the following: 1.Liquids: Capacity of an individual vessel exceeds 55 gallons (208 L) or the aggregate capacity of multiple vessels exceeds 1,000 gallons (3785 L); and 2.Solids: Capacity of an individual vessel exceeds 550 pounds (250 kg) or the aggregate capacity of multiple vessels exceeds 10,000 pounds (4540 kg). | (N)5004.2.2 Secondary containment for hazardous material liquids and solids. (Section deleted) |  |  | 5004.2.2 Secondary containment for hazardous material liquids and solids. Where required by the applicable building code secondary containment devices shall be maintained as approved by the applicable building code.
TABLE 5004.2.2 REQUIRED SECONDARY CONTAINMENT—HAZARDOUS MATERIAL SOLIDS AND LIQUIDS STORAGE | (N)Table 5004.2.2 REQUIRED SECONDARY CONTAINMENT—HAZARDOUS MATERIAL SOLIDS AND LIQUIDS STORAGE (Table deleted)
5004.2.2.1 Containment and drainage methods. The building, room or area shall contain or drain the hazardous materials and fire protection water through the use of one of the following methods: 1.Liquid-tight sloped or recessed floors in indoor locations or similar areas in outdoor locations. 2.Liquid-tight floors in indoor locations or similar areas in outdoor locations provided with liquid-tight raised or recessed sills or dikes. 3.Sumps and collection systems. 4.Drainage systems leading to an approved location. 5.Other approved engineered systems. | (N)5004.2.2.1 Containment and drainage methods. (Section deleted) |  |  | 5004.2.2.1 Containment and drainage methods. Where required by the applicable building code the facilities, equipment, and method used for containment and drainage shall be maintained in accordance with this Chapter and the applicable building code.building,
5004.2.2.3 Indoor design. Secondary containment for indoor storage areas shall be designed to contain a spill from the largest vessel plus the design flow volume of fire protection water calculated to discharge from the fire-extinguishing system over the minimum required system design area or area of the room or area in which the storage is located, whichever is smaller. The containment capacity shall be designed to contain the flow for a period of 20 minutes. | (N)5004.2.2.3 Indoor design. (Section deleted) |  |  | 5004.2.2.3 Indoor design. Where required by the applicable building code the secondary containment for indoor storage areas shall be maintained in accordance with this Chapter and as approved by the applicable building code.
5004.2.2.5 Monitoring. An approved monitoring method shall be provided to detect hazardous materials in the secondary containment system. The monitoring method is allowed to be visual inspection of the primary or secondary containment, or other approved means. Where secondary containment is subject to the intrusion of water, a monitoring method for detecting water shall be provided. Where monitoring devices are provided, they shall be connected to approved visual or audible alarms. | (N)5004.2.2.5 Monitoring (Section deleted) |  |  | 5004.2.2.5 Monitoring. Where monitoring is required by the applicable building code to detect hazardous materials in the secondary containment system the monitoring method is allowed to be visual inspection of the primary or secondary containment, or other approved means and be maintained in accordance with this Chapter and as approved by the applicable building code. Where secondary containment is subject to the intrusion of water, a monitoring method for detecting water shall be provided in accordance with this Chapter and the applicable building code. Where monitoring devices are provided, they shall be connected to visual or audible alarms as required by the applicable building code and be maintained in accordance with this Chapter and as approved by the applicable building code.
5004.2.2.6 Drainage system design. Drainage systems shall be in accordance with the International Plumbing Code and all of the following: 1.The slope of floors to drains in indoor locations, or similar areas in outdoor locations shall not be less than 1 percent. 2.Drains from indoor storage areas shall be sized to carry the volume of the fire protection water as determined by the design density discharged from the automatic fire-extinguishing system over the minimum required system design area or area of the room or area in which the storage is located, whichever is smaller. 3.Drains from outdoor storage areas shall be sized to carry the volume of the fire flow and the volume of a 24-hour rainfall as determined by a 25-year storm. 4.Materials of construction for drainage systems shall be compatible with the materials stored. 5.Incompatible materials used in open systems shall be separated from each other in the drainage system. 6.Drains shall terminate in an approved location away from buildings, valves, means of egress, fire access roadways, adjoining property and storm drains. | (N)5004.2.2.6 Drainage system design. Drainage systems shall be in accordance with the applicable building code. |  |  | 5004.2.2.6 Drainage system design. Drainage systems shall be designed in accordance with the applicable building code and maintained in accordance with this Chapter.
5004.3 Ventilation. Indoor storage areas and storage buildings shall be provided with mechanical exhaust ventilation or natural ventilation where natural ventilation can be shown to be acceptable for the materials as stored. Exception: Storage areas for flammable solids complying with Chapter 59. | (N)5004.3 Ventilation. Ventilation required for indoor storage areas and storage buildings shall be maintained in accordance with the applicable building code. |  |  | 5004.3 Ventilation. Where ventilation is required for indoor storage areas and storage buildings by the applicable building code it shall be maintained in this Chapter and as approved by the applicable building code.
5004.3.1 System requirements. Exhaust ventilation systems shall comply with all of the following: 1.Installation shall be in accordance with the International Mechanical Code. 2.Mechanical ventilation shall be at a rate of not less than 1 cubic foot per minute per square foot [0.00508 m3/(s • m2)] of floor area over the storage area. 3.Systems shall operate continuously unless alternative designs are approved. 4.A manual shutoff control shall be provided outside of the room in a position adjacent to the access door to the room or in an approved location. The switch shall be a break-glass or other approved type and shall be labeled: VENTILATION SYSTEM EMERGENCY SHUTOFF. 5.Exhaust ventilation shall be designed to consider the density of the potential fumes or vapors released. For fumes or vapors that are heavier than air, exhaust shall be taken from a point within 12 inches (305 mm) of the floor. For fumes or vapors that are lighter than air, exhaust shall be taken from a point within 12 inches (305 mm) of the highest point of the room. 6.The location of both the exhaust and inlet air openings shall be designed to provide air movement across all portions of the floor or room to prevent the accumulation of vapors. 7.Exhaust air shall not be recirculated to occupied areas if the materials stored are capable of emitting hazardous vapors and contaminants have not been removed. Air contaminated with explosive or flammable vapors, fumes or dusts; flammable, highly toxic or toxic gases; or radioactive materials shall not be recirculated. | (N)5004.3.1 System requirements. (Section deleted) |  |  | 5004.3.1 System requirements. Where required by the applicable building code exhaust ventilation systems shall be maintained in accordance with this Chapter and as approved by the applicable building code.
5004.5 Automatic sprinkler systems. Indoor storage areas and storage buildings shall be equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1. The design of the sprinkler system shall not be less than that required for Ordinary Hazard Group 2 with a minimum design area of 3,000 square feet (279 m2). Where the materials or storage arrangement are required by other regulations to be provided with a higher level of sprinkler system protection, the higher level of sprinkler system protection shall be provided. | (N)5004.5 Automatic sprinkler systems. Automatic sprinkler systems for the storage of hazardous materials shall be maintained in accordance with the applicable building code. |  |  | 5004.5 Automatic sprinkler systems. Automatic sprinkler systems for the storage of hazardous materials shall be maintained in accordance with with this Chapter and as approved by the applicable building code.
5004.6 Explosion control. Indoor storage rooms, areas and buildings shall be provided with explosion control in accordance with Section 911. | (N)5004.6 Explosion control. Explosion control for storage rooms, areas and buildings shall be maintained in accordance with the applicable building code. |  |  | 5004.6 Explosion control.Where explosion control is required for storage rooms, areas and buildings it shall be maintained in accordance this Chapter and as approved by the applicable building code.
5004.7 Standby or emergency power. Where mechanical ventilation, treatment systems, temperature control, alarm, detection or other electrically operated systems are required, such systems shall be provided with an emergency or standby power system in accordance with NFPA 70 and Section 604. Exceptions: 1.Mechanical ventilation for storage of Class IB and Class IC flammable and combustible liquids in closed containers not exceeding 61/2 gallons (25 L) capacity. 2.Storage areas for Class 1 and 2 oxidizers. 3.Storage areas for Class II, III, IV and V organic peroxides. 4.Storage areas for asphyxiant, irritant and radioactive gases. 5.For storage areas for highly toxic or toxic materials, see Sections 6004.2.2.8 and 6004.3.4.2. 6.Standby power for mechanical ventilation, treatment systems and temperature control systems shall not be required where an approved fail-safe engineered system is installed. | (N)5004.7 Standby or emergency power. Standby or emergency power shall be maintained in accordance with the applicable building code. |  |  | 5004.7 Standby or emergency power. Where mechanical ventilation, treatment systems, temperature control, alarm, detection or other electrically operated systems are required by the applicable building code, such systems shall be provided with an emergency or standby power system in accordance with NFPA 70, Section 604, as approved by the applicable building code.
None | (N)5004.7.1 Exempt applications. (Section deleted)
None | (N)5004.7.2 Fail-safe engineered systems. (Section deleted)
5004.8 Limit controls. Limit controls shall be provided in accordance with Sections 5004.8.1 and 5004.8.2. | (N)5004.8 Limit controls. Limit controls shall be maintained in accordance with the applicable building code. |  |  | 5004.8 Limit controls. Where limit controls are required by the applicable building code they shall be maintained in accordance this Chapter and as approved by the applicable building code.
5004.8.1 Temperature control. Materials that must be kept at temperatures other than normal ambient temperatures to prevent a hazardous reaction shall be provided with an approved means to maintain the temperature within a safe range. Redundant temperature control equipment that will operate on failure of the primary temperature control system shall be provided. Where approved, alternative means that prevent a hazardous reaction are allowed. | (N)5004.8.1 Temperature control. (Section deleted) |  |  | 5004.8.1 Temperature control. Where materials that must be kept at temperatures other than normal ambient temperatures to prevent a hazardous reaction are provided with a means to maintain the temperature within a safe range method shall be maintained in accordance with this Chapter and as approved by the applicable building code.
5004.8.2 Pressure control. Stationary tanks and equipment containing hazardous material liquids that can generate pressures exceeding design limits because of exposure fires or internal reaction shall have some form of construction or other approved means that will relieve excessive internal pressure. The means of pressure relief shall vent to an approved location or to an exhaust scrubber or treatment system where required by Chapter 60. | (N)5004.8.2 Pressure control. (Section deleted) |  |  | 5004.8.2 Pressure control. Where stationary tanks and equipment containing hazardous material liquids that can generate pressures exceeding design limits because of exposure fires or internal reaction shall be maintained by this Chapter, Chapter 60, and as approved by the applicable building code.
5004.9 Emergency alarm. An approved manual emergency alarm system shall be provided in buildings, rooms or areas used for storage of hazardous materials. Emergency alarm-initiating devices shall be installed outside of each interior exit or exit access door of storage buildings, rooms or areas. Activation of an emergency alarm-initiating device shall sound a local alarm to alert occupants of an emergency situation involving hazardous materials. | (N)5004.9 Emergency alarm. Emergency alarm systems shall be maintained in accordance with the applicable building code. |  |  | 5004.9 Emergency alarm. An approved manual emergency alarm system shall be provided in buildings, rooms or areas used for storage of hazardous materials. Emergency alarm-initiating devices shall be installed outside of each interior exit or exit access door of storage buildings, rooms or areas. Activation of an emergency alarm-initiating device shall sound a local alarm to alert occupants of an emergency situation involving hazardous materials.
5004.10 Supervision and monitoring. Emergency alarm, detection and automatic fire-extinguishing systems required by Section 5004 shall be electrically supervised and monitored by an approved supervising station or, when approved, shall initiate an audible and visual signal at a constantly attended on-site location. | (N)5004.10 Supervision and monitoring. (Section deleted) |  |  | 5004.10 Supervision and monitoring. Where emergency alarm, detection and automatic fire-extinguishing systems are required by the applicable building code they shall be maintained in accordance with this Chapter and as approved by the applicable building code.
5004.12 Noncombustible floor. Except for surfacing, floors of storage areas shall be of noncombustible construction. | (N)5004.12 Noncombustible floor. (Section deleted) |  |  | 5004.12 Floors. Floors shall be maintained in accordance with this Chapter and as approved by applicable building code.
5004.13 Weather protection. Where overhead noncombustible construction is provided for sheltering outdoor hazardous material storage areas, such storage shall not be considered indoor storage when the area is constructed in accordance with the requirements for weather protection as required by the International Building Code. | (N)5004.13 Weather protection. Where overhead noncombustible construction is provided for sheltering outdoor hazardous material storage areas, such storage shall not be considered indoor storage where the area is constructed in accordance with the requirements for weather protection as required by the applicable building code. Exception: Storage of explosive materials shall be considered as indoor storage. |  |  | 5004.13 Weather protection. Where overhead noncombustible construction is provided for sheltering outdoor hazardous material storage areas, such storage shall not be considered indoor storage where the area is constructed in accordance with the requirements for weather protection as required by the applicable building code and maintained in accordance with this Chapter and the applicable building code. Exception: Storage of explosive materials shall be considered as indoor storage.
5005.1 General. Use, dispensing and handling of hazardous materials in amounts exceeding the maximum allowable quantity per control area set forth in Section 5003.1 shall be in accordance with Sections 5001, 5003 and 5005. Use, dispensing and handling of hazardous materials in amounts not exceeding the maximum allowable quantity per control area set forth in Section 5003.1 shall be in accordance with Sections 5001 and 5003. | (N)5005.1 General. Use, dispensing and handling of hazardous materials shall be maintained in accordance with the applicable building code |  |  | 5005.1 General. Use, dispensing and handling of hazardous materials shall be maintained in accordance this Chapter and as approved by the applicable building code
5005.1.2 Noncombustible floor. Except for surfacing, floors of areas where liquid or solid hazardous materials are dispensed or used in open systems shall be of noncombustible, liquid-tight construction. | (N)5005.1.2 Noncombustible floor. (Section deleted) |  |  | 5005.1.2 Noncombustible floors. Floors shall be maintained in accordance with this Chapter and thas approved by the applicable building code.
5005.1.3 Spill control and secondary containment for hazardous material liquids. Where required by other provisions of Section 5005, spill control and secondary containment shall be provided for hazardous material liquids in accordance with Section 5004.2. | (N)5005.1.3 Spill control and secondary containment for hazardous material liquids. Where required by the applicable building code, spill control and secondary containment shall be maintained in accordance with the applicable building code. |  |  | 5005.1.3 Spill control and secondary containment for hazardous material liquids. Where required by the applicable building code, spill control and secondary containment shall be maintained in accordance with this Chapter and as approved by the applicable building code.
5005.1.4 Limit controls. Limit controls shall be provided in accordance with Sections 5005.1.4.1 through 5005.1.4.4. | (N)5005.1.4 Limit controls. Limit controls shall be maintained in accordance with the applicable building code. |  |  | 5005.1.4 Limit controls. Where limit controls are required by the applicable building code they shall be maintained in accordance this Chapter and as approved by the applicable building code.
5005.1.4.1 High-liquid-level control. Open tanks in which liquid hazardous materials are used shall be equipped with a liquid-level limit control or other means to prevent overfilling of the tank. | (N)5005.1.4.1 High-liquid-level control. (Section deleted) |  |  | 5005.1.4.1 High-liquid-level control. Open tanks in which liquid hazardous materials are used shall be equipped with a liquid-level limit control or other means to prevent overfilling of the tank as required by the applicable building code and maintained in accordance with this Chapter and as approved by the applicable building code.
5005.1.4.2 Low-liquid-level control. Approved safeguards shall be provided to prevent a low-liquid level in a tank from creating a hazardous condition, including but not limited to, overheating of a tank or its contents. | (N)5005.1.4.2 Low-liquid-level control. (Section deleted) |  |  | 5005.1.4.2 Low-liquid-level control. Where the applicable building code requires safeguards to be provided to prevent a low-liquid level in a tank from creating a hazardous condition, including but not limited to, overheating of a tank or its contents sucjh safeguards shall be maintained in accordance with this Chapter and as approved by the applicable building code.
5005.1.4.3 Temperature control. Temperature control shall be provided in accordance with Section 5004.8.1. | (N)5005.1.4.3 Temperature control. (Section deleted) |  |  | 5005.1.4.3 Temperature control. Where temperature controls are required by the applicable building code they shall be maintained in accordance with this Chapter and as approved by the applicable building code.
5005.1.4.4 Pressure control. Pressure control shall be provided in accordance with Section 5004.8.2. | (N)5005.1.4.4 Pressure control. (Section deleted) |  |  | 5005.1.4.4 Pressuree control. Where pressure controls are required by the applicable building code they shall be maintained in accordance with this Chapter and as approved by the applicable building code.
5005.1.5 Standby or emergency power. Where mechanical ventilation, treatment systems, temperature control, manual alarm, detection or other electrically operated systems are required, such systems shall be provided with an emergency or standby power system in accordance with NFPA 70 and Section 604. Exceptions: 1.Standby power for mechanical ventilation, treatment systems and temperature control systems shall not be required where an approved fail-safe engineered system is installed. 2.Systems for highly toxic or toxic gases shall be provided with emergency power in accordance with Sections 6004.2.2.8 and 6004.3.4.2. | (N)5005.1.5 Standby or emergency power. Standby or emergency power shall be maintained in accordance with the applicable building code. |  |  | 5005.1.5 Standby or emergency power. Where mechanical ventilation, treatment systems, temperature control, manual alarm, detection or other electrically operated systems are required by the applicable building code and such systems shall are provided with an emergency or standby power system it shall be maintained in accordance with Chapter Chapter 6, NFPA 70 and as approved by the applicable building code.
None | (N)5005.1.5.1 Exempt applications. (Section deleted) |  |  | No change.
5005.1.6 Supervision and monitoring. Manual alarm, detection and automatic fire-extinguishing systems required by other provisions of Section 5005 shall be electrically supervised and monitored by an approved supervisory service or, when approved, shall initiate an audible and visual signal at a constantly attended on-site location. | (N)5005.1.6 Supervision and monitoring. (Section deleted) |  |  | 5005.1.6 Supervision and monitoring. Where manual alarm, detection and automatic fire-extinguishing systems are required by the applicable building code they shall be maintained in accordance with this Chapter, Chapter 9, and as approved by the applicable building code.
5005.1.7 Lighting. Adequate lighting by natural or artificial means shall be provided. | (N)5005.1.7 Lighting. Lighting provided for use, dispensing and handling of hazardous materials shall be maintained in accordance with the applicable building code. |  |  | 5005.1.7 Lighting. Lighting provided for use, dispensing and handling of hazardous materials shall be maintained in accordance with this Chapter, Chapter 6, and as approved by the applicable building code.
5005.1.8 Fire-extinguishing systems. Indoor rooms or areas in which hazardous materials are dispensed or used shall be protected by an automatic fire-extinguishing system in accordance with Chapter 9. Sprinkler system design shall not be less than that required for Ordinary Hazard, Group 2, with a minimum design area of 3,000 square feet (279 m2). Where the materials or storage arrangement are required by other regulations to be provided with a higher level of sprinkler system protection, the higher level of sprinkler system protection shall be provided. | (N)5005.1.8 Fire-extinguishing systems. Fire-extinguishing systems for rooms or areas in which hazardous materials are dispensed or used shall be maintained in accordance with the applicable building code |  |  | 5005.1.8 Fire-extinguishing systems. Where Fire-extinguishing systems for rooms or areas in which hazardous materials are dispensed or used are requried by the applicable building code they shall be maintained in accordance with thjis Chapter, Chapter 9, and as approved by the applicable building code
5005.1.9 Ventilation. Indoor dispensing and use areas shall be provided with exhaust ventilation in accordance with Section 5004.3. Exception: Ventilation is not required for dispensing and use of flammable solids other than finely divided particles. | (N)5005.1.9 Ventilation. Ventilation for indoor dispensing and use areas shall be maintained in accordance with the applicable building code. |  |  | 5005.1.9 Ventilation. Where ventilation for indoor dispensing and use areas is required by the applicable building code it shall be maintained in accordance with this Chapter, and as approved by the applicable building code.
5005.2 Indoor dispensing and use. Indoor dispensing and use of hazardous materials shall be in buildings complying with the International Building Code and in accordance with Section 5005.1 and Sections 5005.2.1 through 5005.2.2.4. | 5005.2 Indoor dispensing and use. Indoor dispensing and use of hazardous materials shall be in buildings complying with the International Building Code and in accordance with Section 5005.1, Sections 5005.2.1 through 5005.2.1.4, and Sections 5005.2.2.1 through 5005.2.2.4. |  |  | No change.
5005.2.1.3 Spill control for hazardous material liquids. Buildings, rooms or areas where hazardous material liquids are dispensed into vessels exceeding a 1.3-gallon (5 L) capacity or used in open systems exceeding a 5.3-gallon (20 L) capacity shall be provided with spill control in accordance with Section 5004.2.1. | 5005.2.1.3 Spill control for hazardous material liquids. Buildings, rooms, or areas where hazardous material liquids are dispensed into vessels exceeding a 1.3-gallon (5 L) capacity or used in open systems exceeding a 5.3-gallon (20 L) capacity shall be provided with spill control in accordance with the applicable building code. |  |  | 5005.2.1.3 Spill control for hazardous material liquids. Buildings, rooms, or areas where hazardous material liquids are dispensed into vessels exceeding a 1.3-gallon (5 L) capacity or used in open systems exceeding a 5.3-gallon (20 L) capacity shall be provided with spill control in accordance with this Chapter and as approved by the applicable building code.
5005.2.1.4 Secondary containment for hazardous material liquids. Where required by Table 5005.2.1.4, buildings, rooms or areas where hazardous material liquids are dispensed or used in open systems shall be provided with secondary containment in accordance with Section 5004.2.2 when the capacity of an individual vessel or system or the capacity of multiple vessels or systems exceeds the following: 1.Individual vessel or system: greater than 1.3 gallons (5 L). 2.Multiple vessels or systems: greater than 5.3 gallons (20 L). | (N)5005.2.1.4 Secondary containment for hazardous material liquids. Where required by the applicable building code, secondary containment for buildings, rooms or areas where hazardous material liquids are dispensed or used in open systems shall be maintained in accordance with the applicable building code. |  |  | (N)5005.2.1.4 Secondary containment for hazardous material liquids. Where required by the applicable building code, secondary containment for buildings, rooms or areas where hazardous material liquids are dispensed or used in open systems shall be maintained in accordance with this Chapter and as approved by the applicable building code.
TABLE 5005.2.1.4 REQUIRED SECONDARY CONTAINMENT—HAZARDOUS MATERIAL LIQUIDS USE | (N)TABLE 5005.2.1.4 REQUIRED SECONDARY CONTAINMENT—HAZARDOUS MATERIAL LIQUIDS USE (Table deleted)
5005.2.2 Closed systems. Use of hazardous materials in closed containers or systems shall be in accordance with Sections 5005.2.2.1 through 5005.2.2.4. | (N)5005.2.2 Closed systems. (Section deleted) |  |  | 5005.2.2 Closed systems. Use of hazardous materials in closed containers or systems shall be in accordance with Sections 5005.2.2.1 through 5005.2.2.4.and as approved by the applicable building code.
5005.2.2.1 Ventilation. Where closed systems are designed to be opened as part of normal operations, ventilation shall be provided in accordance with Section 5005.2.1.1. | (N)5005.2.2.1 Ventilation. Ventilation for closed systems shall be maintained in accordance with the applicable building code. |  |  | 5005.2.2.1 Ventilation. Where closed systems are designed to be opened as part of normal operations, ventilation, where required by the applicable building code, shall be maintained in accordance with Section 5005.2.1.1 and as approved by the applicable code.
5005.2.2.2 Explosion control. Explosion control shall be provided in accordance with Section 5004.6 where an explosive environment exists because of the hazardous materials dispensed or used, or as a result of the dispensing or use process. Exception: Where process vessels are designed to contain fully the worst-case explosion anticipated within the vessel under process conditions based on the most likely failure. | (N)5005.2.2.2 Explosion control. Explosion control shall be maintained in accordance with the applicable building code. |  |  | 5005.2.2.2 Explosion control.Where explosion control is required fit shall be maintained in accordance this Chapter and as approved by the applicable building code.
5005.2.2.3 Spill control for hazardous material liquids. Buildings, rooms or areas where hazardous material liquids are used in individual vessels exceeding a 55-gallon (208 L) capacity shall be provided with spill control in accordance with Section 5004.2.1. | (N)5005.2.2.3 Spill control for hazardous material liquids. Spill control for buildings, rooms or areas where hazardous material liquids are used shall be maintained in accordance with the applicable building code. |  |  | 5005.2.2.3 Spill control for hazardous material liquids. Where required by the applicable buildind code spill control for buildings, rooms or areas where hazardous material liquids are used shall be maintained in accordance with this Chapter and as approved by the applicable building code.
5005.2.2.4 Secondary containment for hazardous material liquids. Where required by Table 5005.2.1.4, buildings, rooms or areas where hazardous material liquids are used in vessels or systems shall be provided with secondary containment in accordance with Section 5004.2.2 when the capacity of an individual vessel or system or the capacity of multiple vessels or systems exceeds the following: 1.Individual vessel or system: greater than 55 gallons (208 L). 2.Multiple vessels or systems: greater than 1,000 gallons (3785 L). | (N)5005.2.2.4 Secondary containment for hazardous material liquids. Secondary containment for buildings, rooms or areas where hazardous material liquids are used shall be maintained in accordance with the applicable building code. |  |  | 5005.2.2.4 Secondary containment for hazardous material liquids. Where secondary containment for buildings, rooms or areas where hazardous material liquids are used is required by the applicable building code it shall be maintained in accordance with this Chapter and as approved by the applicable building code.
5005.3.4 Spill control for hazardous material liquids in open systems. Outdoor areas where hazardous material liquids are dispensed in vessels exceeding a 1.3-gallon (5 L) capacity or used in open systems exceeding a 5.3-gallon (20 L) capacity shall be provided with spill control in accordance with Section 5004.2.1. | 5005.3.4 Spill control for hazardous material liquids in open systems. Outdoor areas where hazardous material liquids are dispensed in vessels exceeding a 1.3-gallon (5 L) capacity or used in open systems exceeding a 5.3-gallon (20 L) capacity shall be provided with spill control in accordance with the applicable building code. |  |  | 5005.3.4 Spill control for hazardous material liquids in open systems. Outdoor areas where hazardous material liquids are dispensed in vessels exceeding a 1.3-gallon (5 L) capacity or used in open systems exceeding a 5.3-gallon (20 L) capacity is provided with spill control in accordance with the applicable building code it shall be maintained in accordance with this Chapter and as approved by the applicable building code.
5005.3.5 Secondary containment for hazardous material liquids in open systems. Where required by Table 5005.2.1.4, outdoor areas where hazardous material liquids are dispensed or used in open systems shall be provided with secondary containment in accordance with Section 5004.2.2 when the capacity of an individual vessel or system or the capacity of multiple vessels or systems exceeds the following: 1.Individual vessel or system: greater than 1.3 gallons (5 L). 2.Multiple vessels or systems: greater than 5.3 gallons (20 L). | 5005.3.5 Secondary containment for hazardous material liquids in open systems. Where required, outdoor areas where hazardous material liquids are dispensed or used in open systems shall be provided with secondary containment in accordance with the applicable building code where the capacity of an individual vessel or system or the capacity of multiple vessels or systems exceeds the following: 1. Individual vessel or system: greater than 1.3 gallons (5 L). 2. Multiple vessels or systems: greater than 5.3 gallons (20 L). |  |  | 5005.3.5 Secondary containment for hazardous material liquids in open systems. Where required, outdoor areas where hazardous material liquids are dispensed or used in open systems, shall be provided with secondary containment in accordance with the applicable building code where the capacity of an individual vessel or system or the capacity of multiple vessels or systems exceeds the following: 1. Individual vessel or system: greater than 1.3 gallons (5 L). 2. Multiple vessels or systems: greater than 5.3 gallons (20 L). Such secondary containment shall be maintained in accordance with this Chapter or as approved by the applicable building code.
5005.3.6 Spill control for hazardous material liquids in closed systems. Outdoor areas where hazardous material liquids are used in closed systems exceeding 55 gallons (208 L) shall be provided with spill control in accordance with Section 5004.2.1. | 5005.3.6 Spill control for hazardous material liquids in closed systems. Outdoor areas where hazardous material liquids are used in closed systems exceeding 55 gallons (208 L) shall be provided with spill control in accordance with the applicable building code. |  |  | 5005.3.6 Spill control for hazardous material liquids in closed systems. Outdoor areas where hazardous material liquids are used in closed systems exceeding 55 gallons (208 L) shall be provided with spill control in accordance with the applicable building code. Such spill control shall be maintained in accordance with this Chapter and as approved by the applicable building code.
5005.3.7 Secondary containment for hazardous material liquids in closed systems. Where required by Table 5005.2.1.4, outdoor areas where hazardous material liquids are dispensed or used in closed systems shall be provided with secondary containment in accordance with Section 5004.2.2 when the capacity of an individual vessel or system or the capacity of multiple vessels or systems exceeds the following: 1.Individual vessel or system: greater than 55 gallons (208 L). 2.Multiple vessels or systems: greater than 1,000 gallons (3785 L). | 5005.3.7 Secondary containment for hazardous material liquids in closed systems. Where required, outdoor areas where hazardous material liquids are dispensed or used in closed systems shall be provided with secondary containment in accordance with the applicable building code where the capacity of an individual vessel or system or the capacity of multiple vessels or systems exceeds the following: 1. Individual vessel or system greater than 55 gallons (208 L). 2. Multiple vessels or systems greater than 1,000 gallons (3785 L). |  |  | 5005.3.7 Secondary containment for hazardous material liquids in closed systems. Where required, outdoor areas where hazardous material liquids are dispensed or used in closed systems shall be provided with secondary containment in accordance with this Chapter and the applicable building code where the capacity of an individual vessel or system or the capacity of multiple vessels or systems exceeds the following: 1. Individual vessel or system greater than 55 gallons (208 L). 2. Multiple vessels or systems greater than 1,000 gallons (3785 L). Such secondary containment shall be maintained in accordance with this Chapter or as approved by the applicable building code.
5005.3.9 Weather protection. Where overhead noncombustible construction is provided for sheltering outdoor hazardous material use areas, such use shall not be considered indoor use when the area is constructed in accordance with the requirements for weather protection as required in the International Building Code. Exception: Use of explosive materials shall be considered as indoor use. | 5005.3.9 Weather protection. Where overhead noncombustible construction is provided for sheltering outdoor hazardous material use areas, such use shall not be considered indoor use where the area is constructed in accordance with the requirements for weather protection as required in the applicable building code. Exception: Use of explosive materials shall be considered as indoor use. |  |  | 5005.3.9 Weather protection. Where overhead noncombustible construction is provided for sheltering outdoor hazardous material use areas, such use shall not be considered indoor use where the area is constructed in accordance with the requirements for weather protection as required in the applicable building code. Such overhead protection shall be maintained in compliance with this Chapter and as approved by the applicable building code. Exception: Use of explosive materials shall be considered as indoor use.
5005.4 Handling. Handling of hazardous materials shall be in accordance with Sections 5005.4.1 through 5005.4.4. | (N)5005.4 Handling. Handling of hazardous materials shall be maintained in accordance with the applicable building code |  | Handling of hazardous materials is outside the scope of the USBC. | 5005.4 Handling. Handling of hazardous materials shall be in accordance with Sections 5005.4.1 through 5005.4.4.
5005.4.1 Quantities exceeding the maximum allowable quantity per control area. Handling of hazardous materials in indoor and outdoor locations in amounts exceeding the maximum allowable quantity per control area indicated in Tables 5003.1.1(1) through 5003.1.1(4) shall be in accordance with Sections 5001, 5003, 5005.1 and 5005.4. | (N)5005.4.1 Quantities exceeding the maximum allowable quantity per control area. Handling of hazardous materials in outdoor locations in amounts exceeding the maximum allowable quantity per the applicable building code shall be in accordance with Sections 5001, 5003, 5005.1 and 5005.4. |  | Handling of hazardous materials is outside the scope of the USBC. | 5005.4.1 Quantities exceeding the maximum allowable quantity per control area. Handling of hazardous materials in outdoor locations in amounts exceeding the maximum allowable quantity per the applicable building code shall be in accordance with Sections 5001, 5003, 5005.1 and 5005.4.
5005.4.2 Quantities not exceeding the maximum allowable quantity per control area. Handling of hazardous materials in indoor locations in amounts not exceeding the maximum allowable quantity per control area indicated in Tables 5003.1.1(1) and 5003.1.1(2) shall be in accordance with Sections 5001, 5003 and 5005.1. Handling of hazardous materials in outdoor locations in amounts not exceeding the maximum allowable quantity per control area indicated in Tables 5003.1.1(3) and 5003.1.1(4) shall be in accordance with Sections 5001 and 5003. | (N)5005.4.2 Quantities not exceeding the maximum allowable quantity per control area. Handling of hazardous materials in outdoor locations in amounts not exceeding the maximum allowable quantity per the applicable building code shall be in accordance with Sections 5001 and 5003. |  | Handling of hazardous materials is outside the scope of the USBC. | 5005.4.2 Quantities not exceeding the maximum allowable quantity per control area. Handling of hazardous materials in outdoor locations in amounts not exceeding the maximum allowable quantity per the applicable building code shall be in accordance with Sections 5001 and 5003.
5005.4.4 Dispensing, use and handling. Where hazardous materials having a hazard ranking of 3 or 4 in accordance with NFPA 704 are transported through corridors, interior exit stairways or ramps or exit passageways, there shall be an emergency telephone system, a local manual alarm station or an approved alarm-initiating device at not more than 150-foot (45 720 mm) intervals and at each exit and exit access doorway throughout the transport route. The signal shall be relayed to an approved central, proprietary or remote station service or constantly attended on-site location and shall also initiate a local audible alarm. | (N)5005.4.4 Dispensing, use and handling. Where hazardous materials having a hazard ranking of 3 or 4 are being transported through corridors, interior exit stairways or ramps or exit passageways, such transportation shall be in accordance with the applicable building code. |  | Handling of hazardous materials is outside the scope of the USBC. | 5005.4.4 Dispensing, use and handling. Where hazardous materials having a hazard ranking of 3 or 4 in accordance with NFPA 704 are transported through corridors, interior exit stairways or ramps or exit passageways, there shall be an emergency telephone system, a local manual alarm station or an approved alarm-initiating device at not more than 150-foot (45 720 mm) intervals and at each exit and exit access doorway throughout the transport route. The signal shall be relayed to an approved central, proprietary or remote station service or constantly attended on-site location and shall also initiate a local audible alarm.

## Ch51 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
5101.1 Scope. The provisions of this chapter, the International Building Code and NFPA 30B shall apply to the manufacturing, storage and display of aerosol products. Manufacturing of aerosol products using hazardous materials shall also comply with Chapter 50. | 5101.1 Scope. The provisions of this chapter and NFPA 30B shall apply to the manufacturing, storage and display of aerosol products. Manufacturing of aerosol products using hazardous materials shall also comply with Chapter 50. |  |  | no change
5101.2 Permit required. Permits shall be required as set forth in Section 107.2. | 5101.2 Permit required. Permits shall be required as set forth in Section 107.2. |  |  | no change
5104.1 General. The inside storage of Level 2 and 3 aerosol products shall comply with Sections 5104.2 through 5104.7 and NFPA 30B. Level 1 aerosol products shall be considered equivalent to a Class III commodity and shall comply with the requirements for palletized or rack storage in NFPA 13. | (N)5104.1 General. The inside storage of Levels 2 and 3 aerosol products shall be maintained in accordance with the applicable building code. |  |  | 5104.1 General. The inside storage of Levels 2 and 3 aerosol products shall be maintained in accordance with section 5104.2 through 5104.7, NFPA 30B, and remain in accordance with the applicable building code.
None | 5104.1.1 Plastic containers. Aerosol products in plastic containers larger than 4 fluid ounces (118 ml), but not to exceed 33.8 fluid ounces (1000 ml), shall be allowed only where in accordance with this section. The commodity classification shall be Class III commodities, as defined in the applicable NFPA 13 standard where any of the following conditions are met: 1. Base product has no fire point where tested in accordance with ASTM D 92, and nonflammable propellant. 2. Base product has no sustained combustion as tested in accordance with Appendix H, "Method of Testing for Sustained Combustibility," in U.S. Department of Transportation 49 CFR Part 173, and nonflammable propellant. 3. Base product contains up to 20 percent by volume (15.8 percent by weight) of ethanol or isopropyl alcohol, or both, in an aqueous mix, and nonflammable propellant. 4. Base product contains 4 percent by weight or less of an emulsified flammable liquefied gas propellant within an aqueous base. The propellant shall remain emulsified for the life of the product. Where such propellant is not permanently emulsified, the propellant shall be nonflammable. |  |  | no change
5104.2 Storage in Groups A, B, E, F, I and R. Storage of Level 2 and 3 aerosol products in occupancies in Groups A, B, E, F, I and R shall be limited to the following maximum quantities: 1.A net weight of 1,000 pounds (454 kg) of Level 2 aerosol products. 2.A net weight of 500 pounds (227 kg) of Level 3 aerosol products. 3.A combined net weight of 1,000 pounds (454 kg) of Level 2 and 3 aerosol products. The maximum quantity shall be increased 100 percent where the excess quantity is stored in storage cabinets in accordance with Section 5704.3.2. | (N)5104.2 Storage in Groups A, B, E, F, I and R. Storage of aerosol products in occupancies in Groups A, B, E, F, I and R shall be maintained in accordance with the applicable building code. |  |  | Unless otherwise approved by the applicable building code, storage of Level 2 and 3 aerosol products in occupancies in Groups A, B, E, F, I and R shall be limited to the following maximum quantities: 1.A net weight of 1,000 pounds (454 kg) of Level 2 aerosol products. 2.A net weight of 500 pounds (227 kg) of Level 3 aerosol products. 3.A combined net weight of 1,000 pounds (454 kg) of Level 2 and 3 aerosol products. The maximum quantity shall be increased 100 percent where the excess quantity is stored in storage cabinets in accordance with Section 5704.3.2
5104.2.1 Excess storage. Storage of quantities exceeding the maximum quantities indicated in Section 5104.2 shall be stored in separate inside flammable liquid storage rooms in accordance with Section 5104.5. | 5104.2.1 Excess storage. Storage of quantities exceeding the maximum quantities indicated in Section 5104.2 shall be stored in separate inside flammable liquid storage rooms in accordance with Section 5104.5 |  |  | no change
5104.3 Storage in general purpose warehouses. Aerosol storage in general purpose warehouses utilized only for warehousing-type operations involving mixed commodities shall comply with Section 5104.3.1 or 5104.3.2. | (N)5104.3 Storage in general purpose warehouses. Aerosol storage in general purpose warehouses shall be maintained in accordance with the applicable building code. |  |  | 5104.3 Storage in general purpose warehouses. Aerosol storage in general purpose warehouses utilized only for warehousing-type operations involving mixed commodities shall be maintained in accordance with Section 5104.3.1 or 5104.3.2 and remain in accordance with the applicable building code.
5104.3.1 Nonsegregated storage. Storage consisting of solid pile, palletized or rack storage of Level 2 and 3 aerosol products not segregated into areas utilized exclusively for the storage of aerosols shall comply with Table 5104.3.1. | (N)5104.3.1 Nonsegregated storage. Nonsegregated storage areas shall be maintained in accordance with the applicable building code. |  |  | 5104.3.1 Nonsegregated storage. Unless otherwise approved by the applicable building code, storage consisting of solid pile, palletized or rack storage of Level 2 and 3 aerosol products not segregated into areas utilized exclusively for the storage of aerosols shall comply with Table 5104.3.1.
TABLE 5104.3.1 NONSEGREGATED STORAGE OF LEVEL 2 AND 3 AEROSOL PRODUCTS IN GENERAL PURPOSE WAREHOUSESb | (N)TABLE 5104.3.1 NONSEGREGATED STORAGE OF LEVEL 2 AND 3 AEROSOL PRODUCTS IN GENERAL PURPOSE WAREHOUSES (Table deleted) |  |  | keep table - operational storage limits
5104.3.2 Segregated storage. Storage of Level 2 and 3 aerosol products segregated into areas utilized exclusively for the storage of aerosols shall comply with Table 5104.3.2 and Sections 5104.3.2.1 and 5104.3.2.2. | (N)5104.3.2 Segregated storage. Segregated storage areas shall be maintained in accordance with the applicable building code. |  |  | 5104.3.2 Segregated storage. Unless otherwise approved by the applicable building code, storage of Level 2 and 3 aerosol products segregated into areas utilized exclusively for the storage of aerosols shall comply with Table 5104.3.2 and Sections 5104.3.2.1 and 5104.3.2.2.
TABLE 5104.3.2 SEGREGATED STORAGE OF LEVEL 2 AND 3 AEROSOL PRODUCTS IN GENERAL PURPOSE WAREHOUSES | (N)TABLE 5104.3.2 SEGREGATED STORAGE OF LEVEL 2 AND 3 AEROSOL PRODUCTS IN GENERAL PURPOSE WAREHOUSES (Table deleted) |  |  | Keep table - operational storage limits
5104.3.2.1 Chain-link fence enclosures. Chain-link fence enclosures required by Table 5104.3.2 shall comply with the following: 1.The fence shall not be less than No. 9 gage steel wire, woven into a maximum 2-inch (51 mm) diamond mesh. 2.The fence shall be installed from the floor to the underside of the roof or ceiling above. 3.Class IV and high-hazard commodities shall be stored outside of the aerosol storage area and a minimum of 8 feet (2438 mm) from the fence. 4.Access openings in the fence shall be provided with either self- or automatic-closing devices or a labyrinth opening arrangement preventing aerosol containers from rocketing through the access openings. 5.Not less than two means of egress shall be provided from the fenced enclosure. | (N)5104.3.2.1 Chain link fence enclosures. Chain link fence enclosures shall be maintained in accordance with the applicable building code. |  |  | 5104.3.2.1 Chain-link fence enclosures. Unless otherwise approved by the applicable building code, chain-link fence enclosures required by Table 5104.3.2 shall be maintained in accordance with the following: 1.The fence shall not be less than No. 9 gage steel wire, woven into a maximum 2-inch (51 mm) diamond mesh. 2.The fence shall be maintained from the floor to the underside of the roof or ceiling above. 3.Class IV and high-hazard commodities shall be stored outside of the aerosol storage area and a minimum of 8 feet (2438 mm) from the fence. 4.Access openings in the fence shall be provided with either self- or automatic-closing devices or a labyrinth opening arrangement preventing aerosol containers from rocketing through the access openings. 5.Not less than two means of egress shall be maintained from the fenced enclosure.
5104.3.2.2 Aisles. The minimum aisle requirements for segregated storage in general purpose warehouses shall comply with Table 5104.3.2.2. | (N)5104.3.2.2 Aisles. The minimum aisle requirements for segregated storage in general purpose warehouses shall be maintained in accordance with the applicable building code. |  |  | 5104.3.2.2 Aisles. The minimum aisle requirements for segregated storage in general purpose warehouses shall be maintained in accordance with Table 5104.3.2.2 and remain in accordance with the applicable building code.
TABLE 5104.3.2.2 SEGREGATED STORAGE AISLE WIDTHS AND DISTANCE TO AISLES IN GENERAL PURPOSE WAREHOUSES | (N)TABLE 5104.3.2.2 SEGREGATED STORAGE AISLE WIDTHS AND DISTANCE TO AISLES IN GENERAL PURPOSE WAREHOUSES (Table deleted) |  |  | Keep table - operational storage limits
5104.4 Storage in aerosol warehouses. The total quantity of Level 2 and 3 aerosol products in a warehouse utilized for the storage, shipping and receiving of aerosol products shall not be restricted in structures complying with Sections 5104.4.1 through 5104.4.4. | (N)5104.4 Storage in aerosol warehouses. The total quantity of Levels 2 and 3 aerosol products in a warehouse utilized for the storage, shipping and receiving of aerosol products shall maintained in accordance with the applicable building code. |  |  | 5104.4 Storage in aerosol warehouses. The total quantity of Level 2 and 3 aerosol products in a warehouse utilized for the storage, shipping and receiving of aerosol products shall not be restricted in structures complying with Sections 5104.4.1 through 5104.4.4.
5104.4.1 Automatic sprinkler system. Aerosol warehouses shall be protected by an approved wet-pipe automatic sprinkler system in accordance with NFPA 30B. Sprinkler protection shall be designed based on the highest classification level of aerosol product present. | (N)5104.4.1 Automatic sprinkler system. Where provided, automatic sprinkler systems protecting aerosol warehouses shall be maintained in accordance with the applicable building code. |  |  | 5104.4.1 Automatic sprinkler system. Aerosol warehouses shall be protected by an approved wet-pipe automatic sprinkler system in accordance with NFPA 30B and the applicable building code. Sprinkler protection shall be designed based on the highest classification level of aerosol product present.
5104.4.2 Pile and palletized storage aisles. Solid pile and palletized storage shall be arranged so the maximum travel distance to an aisle is 25 feet (7620 mm). Aisles shall have a minimum width of 4 feet (1219 mm). | (N)5104.4.2 Pile and palletized storage aisles. Travel distance and aisles serving pile and palletized storage shall be maintained in accordance with the applicable building code. |  |  | 5104.4.2 Pile and palletized storage aisles. Solid pile and palletized storage shall be arranged so the maximum travel distance to an aisle is 25 feet (7620 mm). Aisles shall have a minimum width of 4 feet (1219 mm).
5104.4.3 Rack storage aisles. Rack storage shall be arranged with a minimum aisle width of 8 feet (2438 mm) between rows of racks and 8 feet (2438 mm) between racks and adjacent solid pile or palletized storage. Where early suppression fast-response (ESFR) sprinklers provide automatic sprinkler protection, the minimum aisle width shall be 4 feet (1219 mm). | (N)5104.4.3 Rack storage aisles. Rack storage shall be maintained in accordance with the applicable building code. |  |  | 5104.4.3 Rack storage aisles. Rack storage shall be arranged with a minimum aisle width of 8 feet (2438 mm) between rows of racks and 8 feet (2438 mm) between racks and adjacent solid pile or palletized storage. Where early suppression fast-response (ESFR) sprinklers provide automatic sprinkler protection, the minimum aisle width shall be 4 feet (1219 mm).
5104.4.4 Combustible commodities. Combustible commodities other than flammable and combustible liquids shall be permitted to be stored in an aerosol warehouse. Exception: Flammable and combustible liquids in 1-quart (946 mL) metal containers and smaller shall be permitted to be stored in an aerosol warehouse. | (N)5104.4.4 Combustible commodities. (Section deleted) |  |  | 5104.4.4 Combustible commodities. Combustible commodities other than flammable and combustible liquids shall be permitted to be stored in an aerosol warehouse. Exception: Flammable and combustible liquids in 1-quart (946 mL) metal containers and smaller shall be permitted to be stored in an aerosol warehouse.
5104.5 Storage in inside flammable liquid storage rooms. Inside flammable liquid storage rooms shall comply with Section 5704.3.7. The maximum quantities of aerosol products shall comply with Section 5104.5.1 or 5104.5.2. | (N)5104.5 Storage in inside flammable liquid storage rooms. Inside flammable liquid storage rooms shall be maintained in accordance with the applicable building code. |  |  | 5104.5 Storage in inside flammable liquid storage rooms. Inside flammable liquid storage rooms shall be maintained in accordance with Section 5704.3.7 and remain in accordance with the applicable building code. The maximum quantities of aerosol products shall be maintained in accordance with Section 5104.5.1 or 5104.5.2.
5104.5.1 Storage rooms of 500 square feet or less. The storage of aerosol products in flammable liquid storage rooms less than or equal to 500 square feet (46 m2) in area shall not exceed the following quantities: 1.A net weight of 1,000 pounds (454 kg) of Level 2 aerosol products. 2.A net weight of 500 pounds (227 kg) of Level 3 aerosol products. 3.A combined net weight of 1,000 pounds (454 kg) of Level 2 and 3 aerosol products. 5104.5.2 Storage rooms greater than 500 square feet. The storage of aerosol products in flammable liquid storage rooms greater than 500 square feet (46 m2) in area shall not exceed the following quantities: 1.A net weight of 2,500 pounds (1135 kg) of Level 2 aerosol products. 2.A net weight of 1,000 pounds (454 kg) of Level 3 aerosol products. 3.A combined net weight of 2,500 pounds (1135 kg) of Level 2 and 3 aerosol products. The maximum aggregate storage quantity of Level 2 and 3 aerosol products permitted in separate inside storage rooms protected by an approved automatic sprinkler system in accordance with NFPA 30B shall be 5,000 pounds (2270 kg). | (N)5104.5.1 Storage rooms of 500 square feet or less. (Section deleted) (N)5104.5.2 Storage rooms greater than 500 square feet. (Section deleted) |  |  | 5104.5.1 Storage rooms of 500 square feet or less. The storage of aerosol products in flammable liquid storage rooms less than or equal to 500 square feet (46 m2) in area shall not exceed the following quantities: 1.A net weight of 1,000 pounds (454 kg) of Level 2 aerosol products. 2.A net weight of 500 pounds (227 kg) of Level 3 aerosol products. 3.A combined net weight of 1,000 pounds (454 kg) of Level 2 and 3 aerosol products. 5104.5.2 Storage rooms greater than 500 square feet. The storage of aerosol products in flammable liquid storage rooms greater than 500 square feet (46 m2) in area shall not exceed the following quantities: 1.A net weight of 2,500 pounds (1135 kg) of Level 2 aerosol products. 2.A net weight of 1,000 pounds (454 kg) of Level 3 aerosol products. 3.A combined net weight of 2,500 pounds (1135 kg) of Level 2 and 3 aerosol products. The maximum aggregate storage quantity of Level 2 and 3 aerosol products permitted in separate inside storage rooms protected by an approved automatic sprinkler system in accordance with NFPA 30B shall be 5,000 pounds (2270 kg).
5104.6 Storage in liquid warehouses. The storage of Level 2 and 3 aerosol products in liquid warehouses shall comply with NFPA 30B. The storage shall be located within segregated storage areas in accordance with Section 5104.3.2 and Sections 5104.6.1 through 5104.6.3. 5104.6.1 Containment. Spill control or drainage shall be provided to prevent the flow of liquid to within 8 feet (2438 mm) of the segregated storage area. | (N)5104.6 Storage in liquid warehouses. The storage of aerosol products in liquid warehouses shall be maintained in accordance with the applicable building code. (N)5104.6.1 Containment. Spill control or drainage shall be maintained in accordance with the applicable building code. |  |  | 5104.6 Storage in liquid warehouses. The storage of Level 2 and 3 aerosol products in liquid warehouses shall be maintained in accordance with NFPA 30B. Unless otherwise approved by the applicable building code, the storage shall be maintained within segregated storage areas in accordance with Section 5104.3.2 and Sections 5104.6.1 through 5104.6.3. 5104.6.1 Containment. Spill control or drainage shall be maintained to prevent the flow of liquid to within 8 feet (2438 mm) of the segregated storage area.
5104.6.2 Sprinkler design. Sprinkler protection shall be designed based on the highest level of aerosol product present. | (N)5104.6.2 Sprinkler design. (Section deleted) |  |  | 5104.6.2 Sprinkler system. Sprinkler protection shall be maintained in accordance with Chapter 9.
5104.6.3 Opening protection into segregated storage areas. Fire doors or gates opening into the segregated storage area shall either be self-closing or provided with automatic-closing devices activated by sprinkler water flow or an approved fire detection system. | (N)5104.6.3 Opening protection into segregated storage areas. Fire doors or gates opening into the segregated storage area shall be maintained in accordance with the applicable building code. |  |  | 5104.6.3 Opening protection into segregated storage areas. Fire doors or gates opening into the segregated storage area shall be maintained as self-closing or automatic-closing devices activated by sprinkler water flow or an approved fire detection system.
5104.7 Storage in Group M occupancies. Storage of Level 2 and 3 aerosol products in occupancies in Group M shall comply with Table 5104.7. Retail display shall comply with Section 5106. | (N)5104.7 Storage in Group M occupancies. Storage of aerosol products in occupancies in Group M shall be maintained in accordance with the applicable building code. |  |  | 5104.7 Storage in Group M occupancies. Storage of Level 2 and 3 aerosol products in occupancies in Group M shall be maintained in accordance with Table 5104.7 and remain in accordance with the applicable building code. Retail display shall be maintained in accordance with Section 5106.
TABLE 5104.7 MAXIMUM QUANTITIES OF LEVEL 2 AND 3 AEROSOL PRODUCTS IN RETAIL STORAGE AREAS | Delete Table 5104.7. |  |  | Keep table - operational storage limits
5106.1 General. This section shall apply to the retail display of 500 pounds (227 kg) or more of Level 2 and 3 aerosol products. 5106.2 Aerosol display and normal merchandising not exceeding 8 feet (2438 mm) high. Aerosol display and normal merchandising not exceeding 8 feet (2438 mm) in height shall be in accordance with Sections 5106.2.1 through 5106.2.4. 5106.2.1 Maximum quantities in retail display areas. Aerosol products in retail display areas shall not exceed quantities needed for display and normal merchandising and shall not exceed the quantities in Table 5106.2.1. | (N)5106.1 General. This section shall apply to the maintenance of retail display of aerosol products. (N)5106.2.1 Maximum quantities in retail display areas. Quantities of aerosol products in retail display areas shall be maintained in accordance with the applicable building code. |  |  | 5106.1 General. This section shall apply to the retail display of 500 pounds (227 kg) or more of Level 2 and 3 aerosol products. 5106.2 Aerosol display and normal merchandising not exceeding 8 feet (2438 mm) high. Aerosol display and normal merchandising not exceeding 8 feet (2438 mm) in height shall be maintained in accordance with Sections 5106.2.1 through 5106.2.4. 5106.2.1 Maximum quantities in retail display areas. Aerosol products in retail display areas shall not exceed quantities needed for display and normal merchandising and shall not exceed the quantities in Table 5106.2.1.
TABLE 5106.2.1 MAXIMUM QUANTITIES OF LEVEL 2 AND 3 AEROSOL PRODUCTS IN RETAIL DISPLAY AREAS | (N)5106.2.1 MAXIMUM QUANTITIES OF LEVEL 2 AND 3 AEROSOL PRODUCTS IN RETAIL DISPLAY AREAS (Table deleted) |  |  | Keep table - operational storage limits
5106.2.2 Display of containers. Level 2 and 3 aerosol containers shall not be stacked more than 6 feet (1829 mm) high from the base of the aerosol array to the top of the aerosol array unless the containers are placed on fixed shelving or otherwise secured in an approved manner. When storage or retail display is on shelves, the height of such storage or retail display to the top of aerosol containers shall not exceed 8 feet (2438 mm). | (N)5106.2.2 Display of containers. Aerosol containers shall be stacked in accordance with the applicable building code. |  |  | 5106.2.2 Display of containers. Level 2 and 3 aerosol containers shall not be stacked more than 6 feet (1829 mm) high from the base of the aerosol array to the top of the aerosol array unless the containers are placed on fixed shelving or otherwise secured in an approved manner. When storage or retail display is on shelves, the height of such storage or retail display to the top of aerosol containers shall not exceed 8 feet (2438 mm).
5106.2.3 Combustible cartons. Aerosol products located in retail display areas shall be removed from combustible cartons. Exceptions: 1.Display areas that use a portion of combustible cartons that consist of only the bottom panel and not more than 2 inches (51 mm) of the side panel are allowed. 2.When the display area is protected in accordance with Tables 6.3.2.7(a) through 6.3.2.7(l) of NFPA 30B, storage of aerosol products in combustible cartons is allowed. | (N)5106.2.3 Combustible cartons. (Section deleted) |  |  | 5106.2.3 Combustible cartons. Aerosol products located in retail display areas shall be removed from combustible cartons. Exceptions: 1.Display areas that use a portion of combustible cartons that consist of only the bottom panel and not more than 2 inches (51 mm) of the side panel are allowed. 2.When the display area is protected in accordance with Tables 6.3.2.7(a) through 6.3.2.7(l) of NFPA 30B, storage of aerosol products in combustible cartons is allowed
5106.2.4 Retail display automatic sprinkler system. When an automatic sprinkler system is required for the protected retail display of aerosol products, the wet-pipe automatic sprinkler system shall be in accordance with Section 903.3.1.1. The minimum system design shall be for an Ordinary Hazard Group 2 occupancy. The system shall be provided throughout the retail display area. | (N)5106.2.4 Retail display automatic sprinkler system. Where an automatic sprinkler system is required for the protected retail display of aerosol products, the wetpipe automatic sprinkler system shall be in accordance with the applicable building code. |  |  | 5106.2.4 Retail display automatic sprinkler system. When an automatic sprinkler system is required for the protected retail display of aerosol products, the wet-pipe automatic sprinkler system shall be maintained in accordance with Chapter 9 and remain in accordance with NFPA 13 of the applicable building code.
5106.3 Aerosol display and normal merchandising exceeding 8 feet (2438 mm) high. Aerosol display and merchandising exceeding 8 feet in height shall be in accordance with Sections 5106.3.1 through 5106.3.3. 5106.3.1 Maximum quantities in retail display areas. Aerosol products in retail display areas shall not exceed quantities needed for display and normal merchandising and shall not exceed the quantities in Table 5106.2.1, with fire protection in accordance with Section 5106.3.2. 5106.3.2 Automatic sprinkler protection. Aerosol display and merchandising areas shall be protected by an automatic sprinkler system based on the requirements set forth in Tables 6.3.2.7(a) through 6.3.2.7(l) of NFPA 30B and the following: 1.Protection shall be based on the highest level of aerosol product in the array and the packaging method of the storage located more than 6 feet (1829 mm) above the finished floor. 2.When using the cartoned aerosol tables of NFPA 30B, uncartoned or display-cut Level 2 and 3 aerosols shall be permitted not more than 6 feet (1829 mm) above the finished floor. 3.The design area for Level 2 and 3 aerosols shall extend not less than 20 feet (6096 mm) beyond the Level 2 and 3 aerosol display and merchandising areas. 4.Where ordinary and high-temperature ceiling sprinkler systems are adjacent to each other, noncombustible draft curtains shall be installed at the interface. 5106.3.3 Separation of Level 2 and 3 aerosol areas. Separation of Level 2 and 3 aerosol areas shall comply with the following: 1.Level 2 and 3 aerosol display and merchandising areas shall be separated from each other by not less than 25 feet (7620 mm). Also see Table 5106.2.1. 2.Level 2 and 3 aerosol display and merchandising areas shall be separated from flammable and combustible liquids storage and display areas by one or a combination of the following: 2.1.Segregating areas from each other by horizontal distance of not less than 25 feet (7620 mm). 2.2.Isolating areas from each other by a noncombustible partition extending not less than 18 inches (457 mm) above the merchandise. 2.3.In accordance with Section 5106.5. 3.When Item 2.2 above is used to separate Level 2 or 3 aerosols from flammable or combustible liquids, and the aerosol products are located within 25 feet (7620 mm) of flammable or combustible liquids, the area below the noncombustible partition shall be liquid tight at the floor to prevent spilled liquids from flowing beneath the aerosol products. 5106.4 Maximum quantities in storage areas. Aerosol products in storage areas adjacent to retail display areas shall not exceed the quantities in Table 5106.4. | (N)5106.3 Aerosol display and normal merchandising exceeding 8 feet (2438 mm) high. Aerosol display and merchandising exceeding 8 feet in height shall be in accordance with Sections 5106.3.1 through 5106.3.3. (N)5106.3 Aerosol display and normal merchandising exceeding 8 feet (2438 mm) high. Aerosol display and merchandising exceeding 8 feet in height shall be in accordance with Sections 5106.3.1 through 5106.3.3. (N)5106.3.1 Maximum quantities in retail display areas. Aerosol products in retail display areas shall not exceed quantities approved under the applicable building code. (N)5106.3.2 Automatic sprinkler protection. Where provided, automatic sprinkler protection for aerosol display and merchandising areas shall be maintained in accordance with the applicable building code. (N)5106.3.3 Separation of aerosol areas. Separation of aerosol areas shall be maintained in accordance with the applicable building code. (N)5106.4 Maximum quantities in storage areas. Aerosol products in storage areas adjacent to retail display areas shall not exceed the quantities approved under the applicable building code. |  |  | 5106.3 Aerosol display and normal merchandising exceeding 8 feet (2438 mm) high. Aerosol display and merchandising exceeding 8 feet in height shall be maintained in accordance with Sections 5106.3.1 through 5106.3.3. 5106.3.1 Maximum quantities in retail display areas. Aerosol products in retail display areas shall not exceed quantities needed for display and normal merchandising and shall not exceed the quantities in Table 5106.2.1, with fire protection in accordance with Section 5106.3.2. 5106.3.2 Automatic sprinkler protection. Aerosol display and merchandising areas shall be protected by an automatic sprinkler system based on the requirements set forth in Tables 6.3.2.7(a) through 6.3.2.7(l) of NFPA 30B and the following: 1.Protection shall be based on the highest level of aerosol product in the array and the packaging method of the storage located more than 6 feet (1829 mm) above the finished floor. 2.When using the cartoned aerosol tables of NFPA 30B, uncartoned or display-cut Level 2 and 3 aerosols shall be permitted not more than 6 feet (1829 mm) above the finished floor. 3.The design area for Level 2 and 3 aerosols shall extend not less than 20 feet (6096 mm) beyond the Level 2 and 3 aerosol display and merchandising areas. 4.Where ordinary and high-temperature ceiling sprinkler systems are adjacent to each other, noncombustible draft curtains shall be maintained at the interface. 5106.3.3 Separation of Level 2 and 3 aerosol areas. Separation of Level 2 and 3 aerosol areas shall comply with the following: 1.Level 2 and 3 aerosol display and merchandising areas shall be separated from each other by not less than 25 feet (7620 mm). Also see Table 5106.2.1. 2.Level 2 and 3 aerosol display and merchandising areas shall be separated from flammable and combustible liquids storage and display areas by one or a combination of the following: 2.1.Segregating areas from each other by horizontal distance of not less than 25 feet (7620 mm). 2.2.Isolating areas from each other by a noncombustible partition extending not less than 18 inches (457 mm) above the merchandise. 2.3.In accordance with Section 5106.5. 3.When Item 2.2 above is used to separate Level 2 or 3 aerosols from flammable or combustible liquids, and the aerosol products are located within 25 feet (7620 mm) of flammable or combustible liquids, the area below the noncombustible partition shall be liquid tight at the floor to prevent spilled liquids from flowing beneath the aerosol products. 5106.4 Maximum quantities in storage areas. Aerosol products in storage areas adjacent to retail display areas shall not exceed the quantities in Table 5106.4.
TABLE 5106.4 MAXIMUM STORAGE QUANTITIES FOR STORAGE AREAS ADJACENT TO RETAIL DISPLAY OF LEVEL 2 AND 3 AEROSOLS | (N)TABLE 5106.4 MAXIMUM STORAGE QUANTITIES FOR STORAGE AREAS ADJACENT TO RETAIL DISPLAY OF LEVEL 2 AND 3 AEROSOLS (Section deleted) |  |  | Keep table - operational storage limits
5106.5 Special protection design for Level 2 and 3 aerosols adjacent to flammable and combustible liquids in double-row racks. The display and merchandising of Level 2 and 3 aerosols adjacent to flammable and combustible liquids in double-row racks shall be in accordance with Sections 5106.5.1 through 5106.5.8 or Section 5106.3.3. 5106.5.1 Fire protection. Fire protection for the display and merchandising of Level 2 and 3 aerosols in double-row racks shall be in accordance with Table 7.4.1 and Figure 7.4.1 of NFPA 30B. | (N)5106.5 Special protection design for Levels 2 and 3 aerosols adjacent to flammable and combustible liquids in double-row racks. The display and merchandising of aerosols adjacent to flammable and combustible liquids in double-row racks shall be maintained in accordance with the applicable building code. (N)5106.5.1 Fire protection. Where required, fire protection for the display and merchandising of aerosols in double-row racks shall be maintained in accordance with the applicable building code. |  |  | 5106.5 Special protection design for Level 2 and 3 aerosols adjacent to flammable and combustible liquids in double-row racks. The display and merchandising of Level 2 and 3 aerosols adjacent to flammable and combustible liquids in double-row racks shall be maintained in accordance with Sections 5106.5.1 through 5106.5.8 or Section 5106.3.3. 5106.5.1 Fire protection. Fire protection for the display and merchandising of Level 2 and 3 aerosols in double-row racks shall be maintained in accordance with Chapter 9 and remain in accordance with the applicable building code.
5106.5.2 Cartoned products. Level 2 and 3 aerosols displayed or merchandised more than 8 feet (2438 mm) above the finished floor shall be in cartons. | (N)5106.5.2 Cartoned products. (Section deleted) |  |  | 5106.5.2Cartoned products. Level 2 and 3 aerosols displayed or merchandised more than 8 feet (2438 mm) above the finished floor shall be in cartons.
5106.5.3 Shelving. Shelving in racks shall be limited to wire mesh shelving having uniform openings not more than 6 inches (152 mm) apart, with the openings comprising at least 50 percent of the overall shelf area. 5106.5.4 Aisles. Racks shall be arranged so that aisles not less than 71/2 feet (2286 mm) wide are maintained between rows of racks and adjacent solid-piled or palletized merchandise. 5106.5.5 Flue spaces. Flue spaces in racks shall comply with the following: 1.Transverse flue spaces—Nominal 3-inch (76 mm) transverse flue spaces shall be maintained between merchandise and rack uprights. 2.Longitudinal flue spaces—Nominal 6-inch (152 mm) longitudinal flue spaces shall be maintained. 5106.5.6 Horizontal barriers. Horizontal barriers constructed of minimum 3/8-inch-thick (10 mm) plywood or minimum 0.034-inch (0.086 mm) (No. 22 gage) sheet metal shall be provided and located in accordance with Table 7.4.1 and Figure 7.4.1 of NFPA 30B when in-rack sprinklers are installed. | (N)5106.5.3 Shelving. Shelving in racks shall be maintained in accordance with the applicable building code. (N)5106.5.4 Aisles. Aisles shall be maintained between rows of racks and adjacent solidly piled or palletized merchandise in accordance with the applicable building code. (N)5106.5.5 Flue spaces. Flue spaces in racks shall be maintained in accordance with the applicable building code. (N)5106.5.6 Horizontal barriers. Horizontal barriers shall be maintained in accordance with the applicable building code. |  |  | 5106.5.3 Shelving. Unless otherwise approved by the applicable building code, shelving in racks shall be maintained as wire mesh shelving having uniform openings not more than 6 inches (152 mm) apart, with the openings comprising at least 50 percent of the overall shelf area. 5106.5.4 Aisles. Racks shall be maintained so that aisles not less than 71/2 feet (2286 mm) wide are maintained between rows of racks and adjacent solid-piled or palletized merchandise. 5106.5.5 Flue spaces. Flue spaces in racks shall comply with the following: 1.Transverse flue spaces—Nominal 3-inch (76 mm) transverse flue spaces shall be maintained between merchandise and rack uprights. 2.Longitudinal flue spaces—Nominal 6-inch (152 mm) longitudinal flue spaces shall be maintained. 5106.5.6 Horizontal barriers. Horizontal barriers constructed of minimum 3/8-inch-thick (10 mm) plywood or minimum 0.034-inch (0.086 mm) (No. 22 gage) sheet metal shall be maintained in accordance with Table 7.4.1 and Figure 7.4.1 of NFPA 30B when in-rack sprinklers are installed
5106.5.7 Class I, II, III, IV and plastic commodities. Class I, II, III, IV and plastic commodities located adjacent to Level 2 and 3 aerosols shall be protected in accordance with NFPA 13. | (N)5106.5.7 Class I, II, III, IV and plastic commodities. (Section deleted) |  |  | 5106.5.7 Class I, II, III, IV and plastic commodities. Class I, II, III, IV and plastic commodities located adjacent to Level 2 and 3 aerosols shall maintain protection from an approved NFPA 13 sprinkler system in accordance with the applicable building code.
5106.5.8 Flammable and combustible liquids. Class I, II, III A and III B Liquids shall be allowed to be located adjacent to Level 2 and 3 aerosol products when the following conditions are met: 1.Class I, II, IIIA and IIIB liquid containers: Containers for Class I, II, IIIA and IIIB liquids shall be limited to 1.06-gallon (4 L) metal-relieving and nonrelieving style containers and 5.3-gallon (20 L) metal-relieving style containers, and 2.Fire protection for Class I, II, IIIA and IIIB Liquids: Automatic sprinkler protection for Class I, II, IIIA and IIIB liquids shall be in accordance with Chapter 57. | (N)5106.5.8 Flammable and combustible liquids. (Section deleted) |  |  | 5106.5.8 Flammable and combustible liquids. Class I, II, III A and III B Liquids shall be allowed to be maintained adjacent to Level 2 and 3 aerosol products when the following conditions are met: 1.Class I, II, IIIA and IIIB liquid containers: Containers for Class I, II, IIIA and IIIB liquids shall be limited to 1.06-gallon (4 L) metal-relieving and nonrelieving style containers and 5.3-gallon (20 L) metal-relieving style containers, and 2.Fire protection for Class I, II, IIIA and IIIB Liquids: Automatic sprinkler protection for Class I, II, IIIA and IIIB liquids shall be in accordance with Chapter 57.
5107.1 General. Manufacturing facilities shall be in accordance with NFPA 30B. | (N)5107.1 General. Manufacturing facilities shall be maintained in accordance with the applicable building code. |  |  | (N)5107.1 General. Manufacturing facilities shall be maintained in accordance with NFPA30B and remain in accordance with the applicable building code.

## Ch53 (hidden)
``` | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
5301.1 Scope. Storage, use and handling of compressed gases in compressed gas containers, cylinders, tanks and systems shall comply with this chapter, including those gases regulated elsewhere in this code. Partially full compressed gas containers, cylinders or tanks containing residual gases shall be considered as full for the purposes of the controls required. Exceptions: 1.Gases used as refrigerants in refrigeration systems (see Section 606). 2.Compressed natural gas (CNG) for use as a vehicular fuel shall comply with Chapter 23, NFPA 52 and the International Fuel Gas Code. Cutting and welding gases shall also comply with Chapter 35. Cryogenic fluids shall comply with Chapter 55. Liquefied natural gas for use as a vehicular fuel shall also comply with NFPA 52 and NFPA 59A. Compressed gases classified as hazardous materials shall also comply with Chapter 50 for general requirements and chapters addressing specific hazards, including Chapters 58 (Flammable Gases), 60 (Highly Toxic and Toxic Materials), 63 (Oxidizers, Oxidizing Gases and Oxidizing Cryogenic Fluids) and 64 (Pyrophoric Materials). LP-gas shall also comply with Chapter 61 and the International Fuel Gas Code. | 5301.1 Scope. Storage, use and handling of compressed gases in compressed gas containers, cylinders, tanks and systems shall comply with the applicable building code, this chapter, and the use and handling provisions of NFPA 55, including those gases regulated elsewhere in this code. Partially full compressed gas containers, cylinders or tanks containing residual gases shall be considered as full for the purposes of the controls required. Liquefied natural gas for use as a vehicular fuel shall also comply with NFPA 52 and NFPA 59A. Compressed gases classified as hazardous materials shall also comply with Chapter 50 for general requirements and chapters addressing specific hazards, including Chapters 58 (Flammable Gases), 60 (Highly Toxic and Toxic Materials), 63 (Oxidizers, Oxidizing Gases and Oxidizing Cryogenic Fluids), and 64 (Pyrophoric Materials). Compressed hydrogen (CH2) for use as a vehicular fuel shall also comply with Chapters 23 and 58 of this code and NFPA 2. Cutting and welding gases shall also comply with Chapter 35. LP-gas shall also comply with Chapter 61. Exceptions: 1. Gases used as refrigerants in refrigeration systems (see Section 606). 2. Compressed natural gas (CNG) for use as a vehicular fuel shall comply with Chapter 23, NFPA 52, and the International Fuel Gas Code. 3. Cryogenic fluids shall comply with Chapter 55. |  |  | 5301.1 Scope. Storage, use and handling of compressed gases in compressed gas containers, cylinders, tanks and systems shall remain in accordance with the applicable building code and be maintained in accordance with this chapter, and the use and handling provisions of NFPA 55, including those gases regulated elsewhere in this code. Partially full compressed gas containers, cylinders or tanks containing residual gases shall be considered as full for the purposes of the controls required. Liquefied natural gas for use as a vehicular fuel shall also comply with NFPA 52 and NFPA 59A. Compressed gases classified as hazardous materials shall also comply with Chapter 50 for general requirements and chapters addressing specific hazards, including Chapters 58 (Flammable Gases), 60 (Highly Toxic and Toxic Materials), 63 (Oxidizers, Oxidizing Gases and Oxidizing Cryogenic Fluids), and 64 (Pyrophoric Materials). Compressed hydrogen (CH2) for use as a vehicular fuel shall also comply with Chapters 23 and 58 of this code and NFPA 2. Cutting and welding gases shall also comply with Chapter 35. LP-gas shall also comply with Chapter 61. Exceptions: 1. Gases used as refrigerants in refrigeration systems (see Section 606). 2. Compressed natural gas (CNG) for use as a vehicular fuel shall comply with Chapter 23, NFPA 52, and applicable building code. 3. Cryogenic fluids shall comply with Chapter 55.
5301.2 Permits. Permits shall be required as set forth in Section 107.2. | 5301.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
5303.16 Vaults. Generation, compression, storage and dispensing equipment for compressed gases shall be allowed to be located in either above- or below-grade vaults complying with Sections 5303.16.1 through 5303.16.14. | (N)5303.16 Vaults. Vaults shall be maintained in accordance with the applicable building code. |  |  | 5303.16 Vaults. Where approved by the applicable building code, generation, compression, storage and dispensing equipment for compressed gases shall be allowed to be located in either above- or below-grade vaults when maintained in accordance with Sections 5303.16.1 through 5303.16.14.
5303.16.1 Listing required. Vaults shall be listed by a nationally recognized testing laboratory. Exception: Where approved by the fire code official, below-grade vaults are allowed to be constructed on site, provided that the design is in accordance with the International Building Code and that special inspections are conducted to verify structural strength and compliance of the installation with the approved design in accordance with Section 1707 of the International Building Code. Installation plans for below-grade vaults that are constructed on site shall be prepared by, and the design shall bear the stamp of, a professional engineer. Consideration shall be given to soil and hydrostatic loading on the floors, walls and lid; anticipated seismic forces; uplifting by ground water or flooding; and to loads imposed from above, such as traffic and equipment loading on the vault lid. 5303.16.2 Design and construction. The vault shall completely enclose generation, compression, storage or dispensing equipment located in the vault. There shall be no openings in the vault enclosure except those necessary for vault ventilation and access, inspection, filling, emptying or venting of equipment in the vault. The walls and floor of the vault shall be constructed of reinforced concrete at least 6 inches (152 mm) thick. The top of an above-grade vault shall be constructed of noncombustible material and shall be designed to be weaker than the walls of the vault to ensure that the thrust of any explosion occurring inside the vault is directed upward. The top of an at- or below-grade vault shall be designed to relieve safely or contain the force of an explosion occurring inside the vault. The top and floor of the vault and the tank foundation shall be designed to withstand the anticipated loading, including loading from vehicular traffic, where applicable. The walls and floor of a vault installed below grade shall be designed to withstand anticipated soil and hydrostatic loading. Vaults shall be designed to be wind and earthquake resistant, in accordance with the International Building Code. 5303.16.3 Secondary containment. Vaults shall be substantially liquid-tight and there shall be no backfill within the vault. The vault floor shall drain to a sump. For premanufactured vaults, liquid tightness shall be certified as part of the listing provided by a nationally recognized testing laboratory. For field-erected vaults, liquid tightness shall be certified in an approved manner. | (N)5303.16.1 Listing required. (Section deleted) (N)5303.16.2 Design and construction. (Section deleted) (N)5303.16.3 Secondary containment. (Section deleted) |  |  | no change
5303.16.5 Anchoring. Vaults and equipment contained therein shall be suitably anchored to withstand uplifting by groundwater or flooding. The design shall verify that uplifting is prevented even when equipment within the vault is empty. | (N)5303.16.5 Anchoring. (Section deleted) |  |  | no change
5303.16.7 Arrangement. Equipment in vaults shall be listed or approved for above-ground use. Where multiple vaults are provided, adjacent vaults shall be allowed to share a common wall. The common wall shall be liquid and vapor tight and shall be designed to withstand the load imposed when the vault on either side of the wall is filled with water. 5303.16.8 Connections. Connections shall be provided to permit the venting of each vault to dilute, disperse and remove vapors prior to personnel entering the vault. 5303.16.9 Ventilation. Vaults shall be provided with an exhaust ventilation system installed in accordance with Section 5004.3. The ventilation system shall operate continuously or be designed to operate upon activation of the vapor or liquid detection system. The system shall provide ventilation at a rate of not less than 1 cubic foot per minute (cfm) per square foot [0.00508 m3/(s • m2)] of floor area, but not less than 150 cfm (4 m3/min). The exhaust system shall be designed to provide air movement across all parts of the vault floor for gases having a density greater than air and across all parts of the vault ceiling for gases having a density less than air. Supply ducts shall extend to within 3 inches (76 mm), but not more than 12 inches (305 mm), of the floor. Exhaust ducts shall extend to within 3 inches (76 mm), but not more than 12 inches (305 mm) of the floor or ceiling, for heavier-than-air or lighter-than-air gases, respectively. The exhaust system shall be installed in accordance with the International Mechanical Code. 5303.16.10 Monitoring and detection. Vaults shall be provided with approved vapor and liquid detection systems and equipped with on-site audible and visual warning devices with battery backup. Vapor detection systems shall sound an alarm when the system detects vapors that reach or exceed 25 percent of the lower explosive limit (LEL) or one-half the immediately dangerous to life and health (IDLH) concentration for the gas in the vault. Vapor detectors shall be located no higher than 12 inches (305 mm) above the lowest point in the vault for heavier-than-air gases and no lower than 12 inches (305 mm) below the highest point in the vault for lighter-than-air gases. Liquid detection systems shall sound an alarm upon detection of any liquid, including water. Liquid detectors shall be located in accordance with the manufacturers’ instructions. Activation of either vapor or liquid detection systems shall cause a signal to be sounded at an approved, constantly attended location within the facility served by the tanks or at an approved location. Activation of vapor detection systems shall also shut off gas-handling equipment in the vault and dispensers. | (N)5303.16.7 Arrangement. (Section deleted) (N)5303.16.8 Connections. (Section deleted) (N)5303.16.9 Ventilation. (Section deleted) (N)5303.16.10 Monitoring and detection. (Section deleted) |  |  | no change
5303.16.12 Relief vents. Vent pipes for equipment in the vault shall terminate at least 12 feet (3658 mm) above ground level. | (N)5303.16.12 Relief vents. (Section deleted) (N)5303.16.14 Classified area. (Section deleted) |  |  | no change
5303.16.14 Classified area. The interior of a vault containing a flammable gas shall be designated a Class I, Division 1 location, as defined in NFPA 70. | (N)5303.16.14 Classified area. (Section deleted) |  |  | 5303.16.14 Classified area. The interior of a vault containing a flammable gas shall be maintained as a Class I, Division 1 location, as defined in NFPA 70.
5305.5 Venting. Venting of gases shall be directed to an approved location. Venting shall comply with the International Mechanical Code. | (N)5305.5 Venting. Venting shall be maintained in accordance with the applicable building code. |  |  | (N)5305.5 Venting. Venting shall be maintained in accordance with this chapter and remain in accordance with the applicable building code.
5306.2 Interior supply location. Medical gases shall be stored in areas dedicated to the storage of such gases without other storage or uses. Where containers of medical gases in quantities greater than the permit amount are located inside buildings, they shall be in a 1-hour exterior room, a 1-hour interior room or a gas cabinet in accordance with Section 5306.2.1, 5306.2.2 or 5306.2.3, respectively. Rooms or areas where medical gases are stored or used in quantities exceeding the maximum allowable quantity per control area as set forth in Section 5003.1 shall be in accordance with the International Building Code for high-hazard Group H occupancies. | (N)5306.2 Interior supply location. Medical gases shall be stored in areas approved under the applicable building code. |  |  | 5306.2 Interior supply location. Unless otherwise approved by the applicable bulding code, medical gases shall be stored in areas dedicated to the storage of such gases without other storage or uses. Where containers of medical gases in quantities greater than the permit amount are located inside buildings, they shall be remain in protected and ventilated rooms or gas cabinets in accordance with the applicable building code. Rooms or areas where medical gases are stored or used in quantities exceeding the maximum allowable quantity per control area as set forth in Section 5003.1 shall remain in accordance with the applicable building code for high-hazard Group H occupancies.
5306.2.1 One-hour exterior rooms. A 1-hour exterior room shall be a room or enclosure separated from the remainder of the building by fire barriers constructed in accordance with Section 707 of the International Building Code or horizontal assemblies constructed in accordance with Section 711 of the International Building Code, or both, with a fire-resistance rating of not less than 1 hour. Openings between the room or enclosure and interior spaces shall be self-closing smoke- and draft-control assemblies having a fire protection rating of not less than 1 hour. Rooms shall have at least one exterior wall that is provided with at least two vents. Each vent shall not be less than 36 square inches (0.023 m2) in area. One vent shall be within 6 inches (152 mm) of the floor and one shall be within 6 inches (152 mm) of the ceiling. Rooms shall be provided with at least one automatic sprinkler to provide container cooling in case of fire. | (N)5306.2.1 One-hour exterior rooms. (Section deleted) |  |  | no change
5306.2.2 One-hour interior room. When an exterior wall cannot be provided for the room, automatic sprinklers shall be installed within the room. The room shall be exhausted through a duct to the exterior. Supply and exhaust ducts shall be enclosed in a 1-hour-rated shaft enclosure from the room to the exterior. Approved mechanical ventilation shall comply with the International Mechanical Code and be provided at a minimum rate of 1 cubic foot per minute per square foot [0.00508 m3/(s • m2)] of the area of the room. | (N)5306.2.2 One-hour interior room. (Section deleted) |  |  | no change
None | 5307.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
None | (N)5307.5 Required protection. (Section deleted) |  |  | 5307.5 Required protection. Where carbon dioxide storage tanks, cylinders, piping and equipment are located indoors, rooms or areas containing carbon dioxide storage tanks, cylinders, piping and fittings and other areas where a leak of carbon dioxide can collect, such areas shall maintain mechanical ventilation systems or emergency alarm systems and the systems shall remain in accordance with the applicable building code.
None | (N)5307.5.1 Ventilation. Mechanical ventilation shall be maintained in accordance with the applicable building code. (N)5307.5.2 Emergency alarm system. Where required under the applicable building code, emergency alarm systems shall be maintained. |  |  | delete
None | (N)5308.1 General. (Section deleted) |  |  | 5308.1 General. Compressed gases in storage or use not regulated by the material-specific provisions of Chapters 6, 54, 55 and 60 through 67, including asphyxiant, irritant and radioactive gases, shall comply with this section in addition to other requirements of this chapter.
None | (N)5308.2 Ventilation. Where mechanical ventilation is required, it shall be maintained in accordance with the applicable building code |  |  | 5308.2 Ventilation. Indoor storage and use areas and storage buildings shall be maintained with mechanical exhaust ventilation or natural ventilation in accordance with the requirements of the applicable building code. Where mechanical ventilation is provided, the systems shall be operational during such time as the building or space is occupied

## Ch54 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
5401.1 Scope. The storage and use of corrosive materials shall be in accordance with this chapter. Compressed gases shall also comply with Chapter 53. Exceptions: 1.Display and storage in Group M and storage in Group S occupancies complying with Section 5003.11. 2.Stationary storage battery systems in accordance with Section 608. 3.This chapter shall not apply to R-717 (ammonia) where used as a refrigerant in a refrigeration system (see Section 606). | 5401.1 Scope. Maintenance and operational aspects of the storage and use of corrosive materials shall be in accordance with this chapter. Compressed gases shall also comply with Chapter 53. Exceptions: 1. Display and storage in Group M and storage in Group S occupancies complying with Section 5003.11. 2. Stationary storage battery systems in accordance with Section 608. 3. This chapter shall not apply to R-717 (ammonia) where used as a refrigerant in a refrigeration system (see Section 606). |  |  | 5401.1 Scope. The storage and use of corrosive materials shall be in accordance with this chapter. Compressed gases shall also comply with Chapter 53. Exceptions: 1.Display and storage in Group M and storage in Group S occupancies complying with Section 5003.11. 2.Stationary storage battery systems in accordance with Section 608. 3.This chapter shall not apply to R-717 (ammonia) where used as a refrigerant in a refrigeration system (see Section 606).
5401.2 Permits. Permits shall be required as set forth in Section 107.2. | 5401.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
5403.1 Quantities not exceeding the maximum allowable quantity per control area. The storage and use of corrosive materials in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with Sections 5001, 5003 and 5401. 5403.2 Quantities exceeding the maximum allowable quantity per control area. The storage and use of corrosive materials in amounts exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with this chapter and Chapter 50. | 5403.1 Quantities not exceeding the maximum allowable quantity per control area. The storage and use of corrosive materials in amounts not exceeding the maximum allowable quantity per control area shall be in accordance with the applicable building code. 5403.2 Quantities exceeding the maximum allowable quantity per control area. The storage and use of corrosive materials in amounts exceeding the maximum allowable quantity per control area shall be in accordance with the applicable building code. |  |  | 5403.1 Quantities not exceeding the maximum allowable quantity per control area. The storage and use of corrosive materials in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be maintained in accordance with Sections 5001, 5003 and 5401. 5403.2 Quantities exceeding the maximum allowable quantity per control area. The storage and use of corrosive materials in amounts exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be maintained in accordance with this chapter, chapter 50 and remain in accordance with the applicable building code for a high-hazard, group H occupancy.
5404.1.1 Liquid-tight floor. In addition to the provisions of Section 5004.12, floors in storage areas for corrosive liquids shall be of liquid-tight construction. | (N)5404.1.1 Liquid-tight floor. Liquid-tight floors shall be maintained in accordance with the applicable building code. |  |  | 5404.1.1 Liquid-tight floor. In addition to the provisions of Section 5004.12, floors in storage areas for corrosive liquids shall remain as liquid-tight construction in accordance with the applicable building code.
5404.2.1 Above-ground outside storage tanks. Above-ground outside storage tanks exceeding an aggregate quantity of 1,000 gallons (3785 L) of corrosive liquids shall be provided with secondary containment in accordance with Section 5004.2.2. | (N)5404.2.1 Aboveground outside storage tanks. Aboveground outside storage tanks shall be maintained in accordance with the applicable building code. |  |  | 5404.2.1 Above-ground outside storage tanks. Above-ground outside storage tanks exceeding an aggregate quantity of 1,000 gallons (3785 L) of corrosive liquids shall be maintained with secondary containment in accordance with Section 5004.2.2.
5405.1.2 Ventilation. When corrosive materials are dispensed or used, mechanical exhaust ventilation in accordance with Section 5005.2.1.1 shall be provided. | (N)5405.1.2 Ventilation. Where required, mechanical exhaust ventilation shall be maintained in accordance with the applicable building code. |  |  | 5405.1.2 Ventilation. When corrosive materials are dispensed or used, mechanical exhaust ventilation in accordance with the applicable building code shall be maintained.

## Ch55 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
5501.1 Scope. Storage, use and handling of cryogenic fluids shall comply with this chapter. Cryogenic fluids classified as hazardous materials shall also comply with Chapter 50 for general requirements. Partially full containers containing residual cryogenic fluids shall be considered as full for the purposes of the controls required. Exceptions: 1.Fluids used as refrigerants in refrigeration systems (see Section 606). 2.Liquefied natural gas (LNG), which shall comply with NFPA 59A. Oxidizing cryogenic fluids, including oxygen, shall comply with NFPA 55 and Chapter 63, as applicable. Flammable cryogenic fluids, including hydrogen, methane and carbon monoxide, shall comply with NFPA 55 and Chapters 23 and 58, as applicable. Inert cryogenic fluids, including argon, helium and nitrogen, shall comply with CGA P-18. 5501.2 Permits. Permits shall be required as set forth in Section 107.2. | 5501.1 Scope. Maintenance and operational aspects of the storage, use and handling of cryogenic fluids shall comply with this chapter and NFPA 55. Cryogenic fluids classified as hazardous materials shall also comply with the general requirements of Chapter 50. Partially full containers containing residual cryogenic fluids shall be considered as full for the purposes of the controls required. Exceptions: 1. Fluids used as refrigerants in refrigeration systems (see Section 606). 2. Liquefied natural gas (LNG), which shall comply with NFPA 59A. Oxidizing cryogenic fluids, including oxygen, shall comply with Chapter 63, as applicable. Flammable cryogenic fluids, including hydrogen, methane and carbon monoxide, shall comply with Chapters 23 and 58, as applicable. Inert cryogenic fluids, including argon, helium and nitrogen, shall comply with ANSI/CGA P-18. 5501.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
5503.1.2 Concrete containers. Concrete containers shall be built in accordance with the International Building Code. Barrier materials and membranes used in connection with concrete, but not functioning structurally, shall be compatible with the materials contained. | (N)5503.1.2 Concrete containers. Barrier materials and membranes used in connection with concrete, but not functioning structurally, shall be compatible with the materials contained. |  |  | 5503.1.2 Concrete containers. Concrete containers shall comply with the applicable building code. Barrier materials and membranes used in connection with concrete, but not functioning structurally, shall be compatible with the materials contained.
5503.5.2 Securing of containers. Stationary containers shall be secured to foundations in accordance with the International Building Code. Portable containers subject to shifting or upset shall be secured. Nesting shall be an acceptable means of securing containers. | (N)5503.5.2 Securing of containers. Stationary containers shall be secured to foundations in accordance with the applicable building code. Portable containers subject to shifting or upset shall be secured. Nesting shall be an acceptable means of securing containers. |  |  | no change
5503.6 Electrical wiring and equipment. Electrical wiring and equipment shall comply with NFPA 70 and Sections 5503.7.1 and 5503.7.2. | (N)5503.6 Electrical wiring and equipment. Electrical wiring and equipment shall be maintained in accordance with the applicable building code. |  |  | 5503.6 Electrical wiring and equipment. Electrical wiring and equipment shall be maintained in accordance with NFPA 70 and Sections 5503.7.1 and 5503.7.2.
5504.2.1 Stationary containers. Stationary containers shall be installed in accordance with the provisions applicable to the type of fluid stored and this section. | (N)5504.2.1 Stationary containers. Stationary containers shall be maintained in accordance with the applicable building code. |  |  | 5504.2.1 Stationary containers. Stationary containers shall be remain in accordance with the applicable building code and comply with the maintainance provisions of this section and those applicable to the type of fluid stored.
5504.2.1.2 Construction of indoor areas. Cryogenic fluids in stationary containers stored indoors shall be located in buildings, rooms or areas constructed in accordance with the International Building Code. | (N) 5504.2.1.2 Construction of indoor areas. (Section deleted) |  |  | 5504.2.1.2 Indoor storage areas. Cryogenic fluids in stationary containers stored indoors shall remain in buildings, rooms or areas constructed for this use in accordance with the applicable building code.
5504.2.1.3 Ventilation. Storage areas for stationary containers shall be ventilated in accordance with the International Mechanical Code. | (N)5504.2.1.3 Ventilation. Ventilation required in storage areas for stationary containers shall be maintained in accordance with the applicable building code. |  |  | 5504.2.1.3 Ventilation. Storage areas for stationary containers shall be remain ventilated in accordance with the applicable building code.
5504.2.2.2 Construction of indoor areas. Cryogenic fluids in portable containers stored indoors shall be stored in buildings, rooms or areas constructed in accordance with the International Building Code. | (N)5504.2.2.2 Construction of indoor areas. Rooms or areas used for the storage of cryogenic fluids in portable containers shall be maintained in accordance with the applicable building code. |  | portable | 5504.2.2.2 Indoor storage areas. Cryogenic fluids in portable containers stored indoors shall only be stored in buildings, rooms or areas constructed for this use in accordance with the applicable building code.
5504.2.2.3 Ventilation. Storage areas shall be ventilated in accordance with the International Mechanical Code. | (N)5504.2.2.3 Ventilation. Ventilation shall be maintained in accordance with the applicable building code. |  | portable | 5504.2.2.3 Ventilation. Storage areas for portable containers shall be remain ventilated in accordance with the applicable building code.
5505.4.1 Dispensing areas. Dispensing of cryogenic fluids with physical or health hazards shall be conducted in approved locations. Dispensing indoors shall be conducted in areas constructed in accordance with the International Building Code. | (N)5505.4.1 Dispensing areas. Dispensing of cryogenic fluids with physical or health hazards shall be conducted in approved locations. |  |  | no change
5505.4.1.1 Ventilation. Indoor areas where cryogenic fluids are dispensed shall be ventilated in accordance with the requirements of the International Mechanical Code in a manner that captures any vapor at the point of generation. Exception: Cryogenic fluids that can be demonstrated not to create harmful vapors. | (N)5505.4.1.1 Ventilation. Ventilation required in areas where cryogenic fluids are dispensed shall be maintained in accordance with the applicable building code. Exception: Cryogenic fluids that can be demonstrated not to create harmful vapors. |  |  | 5505.4.1.1 Ventilation. Ventilation required by the applicable building code shall be maintained in areas where cryogenic fluids are dispensed. Exception: Cryogenic fluids that can be demonstrated not to create harmful vapors.

## Ch56 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
4.The possession, storage, and use of not more than 15 pounds (6.81 kg) of commercially manufactured sporting black powder, 20 pounds (9 kg) of smokeless powder and any amount of small arms primers for hand loading of small arms ammunition for personal consumption. | Change exception 4 in Section 5601.1 to read: 4. The possession, storage, and use of not more than 15 pounds (6.81 kg) of commercially manufactured sporting black powder, 20 pounds (9 kg) of smokeless powder and any amount of small arms primers for hand loading of small arms ammunition for personal consumption.
10.The storage, handling, or use of explosives or blasting agents pursuant to the provisions of Title 45.1 of the Code of Virginia. 11.The display of small arms primers in Group M when in the original manufacturer’s packaging. 12.The possession, storage and use of not more than 50 pounds (23 kg) of commercially manufactured sporting black powder, 100 pounds (45 kg) of smokeless powder, and small arms primers for hand loading of small arms ammunition for personal consumption in Group R-3 or R-5, or 200 pounds (91 kg) of smokeless powder when stored in the manufacturer’s original containers in detached Group U structures at least 10 feet (3048 mm) from inhabited buildings and are accessory to Group R-3 or R-5. | Add exceptions 10, 11 and 12 to Section 5601.1 to read: 10. The storage, handling, or use of explosives or blasting agents pursuant to the provisions of Title 45.1 of the Code of Virginia. 11. The display of small arms primers in Group M when in the original manufacturer's packaging. 12. The possession, storage and use of not more than 50 pounds (23 kg) of commercially manufactured sporting black powder, 100 pounds (45 kg) of smokeless powder, and small arms primers for hand loading of small arms ammunition for personal consumption in Group R-3 or R-5, or 200 pounds (91 kg) of smokeless powder when stored in the manufacturer's original containers in detached Group U structures at least 10 feet (3048 mm) from inhabited buildings and are accessory to Group R-3 or R-5.
4.The possession, storage, sale, handling and use of permissible fireworks where allowed by applicable local or state laws, ordinances and regulations provided such fireworks comply with CPSC 16 CFR, Parts 1500-1507, and DOTn 49 CFR, Parts 100-178, for consumer fireworks. | Change exception 4 in Section 5601.1.3 to read: 4. The possession, storage, sale, handling and use of permissible fireworks where allowed by applicable local or state laws, ordinances and regulations provided such fireworks comply with CPSC 16 CFR, Parts 1500- 1507, and DOTn 49 CFR, Parts 100-178, for consumer fireworks.
5.The sale or use of materials or equipment when such materials or equipment is used or to be used by any person for signaling or other emergency use in the operation of any boat, railroad train or other vehicle for the transportation of persons or property. | Add exception 5 to Section 5601.1.3 to read: 5. The sale or use of materials or equipment when such materials or equipment is used or to be used by any person for signaling or other emergency use in the operation of any boat, railroad train or other vehicle for the transportation of persons or property.
5601.2 Permit required. Permits shall be required as set forth in Section 107.2 and regulated in accordance with this section. The manufacture, storage, possession, sale and use of fireworks or explosives shall not take place without first applying for and obtaining a permit. 5601.2.1 Residential uses. No person shall keep or store, nor shall any permit be issued to keep, possess or store, any fireworks or explosives at any place of habitation, or within 100 feet (30 480 mm) thereof. Exception: Storage of smokeless propellant, black powder, and small arms primers for personal use and not for resale in accordance with Section 5606. 5601.2.2 Sale and retail display. Except for the Armed Forces of the United States, Coast Guard, National Guard, federal, state and local regulatory, law enforcement and fire agencies acting in their official capacities, explosives shall not be sold, given, delivered or transferred to any person or company not in possession of a valid permit. The holder of a permit to sell explosives shall make a record of all transactions involving explosives in conformance with Section 5603.2 and include the signature of any receiver of the explosives. No person shall construct a retail display nor offer for sale explosives, explosive materials, or fireworks upon highways, sidewalks, public property, or in assembly or educational occupancies. 5601.2.3 Permit restrictions. The fire official is authorized to limit the quantity of explosives, explosive materials, or fireworks permitted at a given location. No person, possessing a permit for storage of explosives at any place, shall keep or store an amount greater than authorized in such permit. Only the kind of explosive specified in such a permit shall be kept or stored. | 5601.2 Permit required. Permits shall be required as set forth in Section 107.2 and regulated in accordance with this section. The manufacture, storage, possession, sale and use of fireworks or explosives shall not take place without first applying for and obtaining a permit. 5601.2.1 Residential uses. No person shall keep or store, nor shall any permit be issued to keep, possess or store, any fireworks or explosives at any place of habitation, or within 100 feet (30,480 mm) thereof. Exception: Storage of smokeless propellant, black powder, and small arms primers for personal use and not for resale in accordance with Section 5606. 5601.2.2 Sale and retail display. Except for the Armed Forces of the United States, Coast Guard, National Guard, federal, state and local regulatory, law enforcement and fire agencies acting in their official capacities, explosives shall not be sold, given, delivered or transferred to any person or company not in possession of a valid permit. The holder of a permit to sell explosives shall make a record of all transactions involving explosives in conformance with Section 5603.2 and include the signature of any receiver of the explosives. No person shall construct a retail display nor offer for sale explosives, explosive materials, or fireworks upon highways, sidewalks, public property, or in assembly or educational occupancies. 5601.2.3 Permit restrictions. The fire official is authorized to limit the quantity of explosives, explosive materials, or fireworks permitted at a given location. No person, possessing a permit for storage of explosives at any place, shall keep or store an amount greater than authorized in such permit. Only the kind of explosive specified in such a permit shall be kept or stored.
5601.2.3.1 Permit applicants. As a condition of a permit as provided for in Section 107.5, the fire official shall not issue a permit to manufacture, store, handle, use or sell explosives or blasting agents to any applicant who has not provided on the permit application the name and signature of a designated individual as representing the applicant. When, as provided for in Section 107.2 or 107.6, a permit is required to conduct a fireworks display, as a condition of permit as provided for in Section 107.5, the fire official shall not issue a permit to design, setup or conduct a fireworks display to any applicant who has not provided on the permit application the name and signature of a designated individual as representing the applicant. If the applicant’s designated individual changes or becomes no longer qualified to represent the applicant as responsible management or designated individual, the applicant shall notify the fire official who issued the permit on the change of status of the designated individual. The notice is to be made prior to the use of any explosives or conducting a fireworks display but in no case shall the notification occur more than 7 days after the change of status and shall provide the name of another designated individual. The fire official may revoke or require the reissuance of a permit based on a change of permit conditions or status or inability to provide another designated individual. 5601.2.3.1.1 BCC. The SFMO shall process all applications for a BCC for compliance with Section 27-97.2 of the Code of Virginia and will be the sole provider of a BCC. Using forms provided by the SFMO, a BCC may be applied for and issued to any person who submits to the completion of a background investigation by providing fingerprints and personal descriptive information to the SFMO. The SFMO shall forward the fingerprints and personal descriptive information to the Central Criminal Records Exchange for submission to the Federal Bureau of Investigation for the purpose of obtaining a national criminal history records check regarding such applicant. 5601.2.3.1.2 Issuance of a BCC. The issuance of a BCC shall be denied if the applicant or designated person representing an applicant has been convicted of any felony, whether such conviction occurred under the laws of the Commonwealth, or any other state, the District of Columbia, the United States or any territory thereof, unless his civil rights have been restored by the Governor or other appropriate authority. 5601.2.3.1.3 Fee for BCC. The fee for obtaining or renewing a BCC from the SFMO shall be $150 plus any additional fees charged by other agencies for fingerprinting and for obtaining a national criminal history record check through the Central Criminal Records Exchange to the Federal Bureau of Investigation. 5601.2.3.1.4 Revocation of a BCC. After issuance of a BCC, subsequent conviction of a felony will be grounds for immediate revocation of a BCC, whether such conviction occurred under the laws of the Commonwealth, or any other state, the District of Columbia, the United States or any territory thereof. The BCC shall be returned to the SFMO immediately. An individual may reapply for his BCC if his civil rights have been restored by the Governor or other appropriate authority. | 5601.2.3.1 Permit applicants. As a condition of a permit as provided for in Section 107.5, the fire official shall not issue a permit to manufacture, store, handle, use or sell explosives or blasting agents to any applicant who has not provided on the permit application the name and signature of a designated individual as representing the applicant. When, as provided for in Section 107.2 or 107.6, a permit is required to conduct a fireworks display, as a condition of permit as provided for in Section 107.5, the fire official shall not issue a permit to design, setup or conduct a fireworks display to any applicant who has not provided on the permit application the name and signature of a designated individual as representing the applicant. If the applicant's designated individual changes or becomes no longer qualified to represent the applicant as responsible management or designated individual, the applicant shall notify the fire official who issued the permit on the change of status of the designated individual. The notice is to be made prior to the use of any explosives or conducting a fireworks display but in no case shall the notification occur more than seven days after the change of status and shall provide the name of another designated individual. The fire official may revoke or require the reissuance of a permit based on a change of permit conditions or status or inability to provide another designated individual. 5601.2.3.1.1 BCC. The SFMO shall process all applications for a BCC for compliance with § 27-97.2 of the Code of Virginia and will be the sole provider of a BCC. Using forms provided by the SFMO, a BCC may be applied for and issued to any person who submits to the completion of a background investigation by providing fingerprints and personal descriptive information to the SFMO. The SFMO shall forward the fingerprints and personal descriptive information to the Central Criminal Records Exchange for submission to the Federal Bureau of Investigation for the purpose of obtaining a national criminal history records check regarding such applicant. 5601.2.3.1.2 Issuance of a BCC. The issuance of a BCC shall be denied if the applicant or designated person representing an applicant has been convicted of any felony, whether such conviction occurred under the laws of the Commonwealth, or any other state, the District of Columbia, the United States or any territory thereof, unless his civil rights have been restored by the Governor or other appropriate authority. 5601.2.3.1.3 Fee for BCC. The fee for obtaining or renewing a BCC from the SFMO shall be $150 plus any additional fees charged by other agencies for fingerprinting and for obtaining a national criminal history record check through the Central Criminal Records Exchange to the Federal Bureau of Investigation. 5601.2.3.1.4 Revocation of a BCC. After issuance of a BCC, subsequent conviction of a felony will be grounds for immediate revocation of a BCC, whether such conviction occurred under the laws of the Commonwealth, or any other state, the District of Columbia, the United States or any territory thereof. The BCC shall be returned to the SFMO immediately. An individual may reapply for his BCC if his civil rights have been restored by the Governor or other appropriate authority.
5601.2.4 Financial responsibility. Before a permit is issued, as required by Section 5601.2, the applicant shall file with the jurisdiction a corporate surety bond in the principal sum of $500,000 or a public liability insurance policy for the same amount, for the purpose of the payment of all damages to persons or property which arise from, or are caused by, the conduct of any act authorized by the permit upon which any judicial judgment results. The legal department of the jurisdiction may specify a greater amount when conditions at the location of use indicate a greater amount is required. Government entities shall be exempt from this bond requirement. 5601.2.4.1 Blasting. Before approval to do blasting is issued, the applicant for approval shall file a bond or submit a certificate of insurance in such form, amount, and coverage as determined by the legal department of the jurisdiction to be adequate in each case to indemnify the jurisdiction against any and all damages arising from permitted blasting but in no case shall the value of the coverage be less than $1,000,000. Exception: Filing a bond or submitting a certificate of liability insurance is not required for blasting on real estate parcels of 5 or more acres conforming to the definition of “real estate devoted to agricultural use” or “real estate devoted to horticultural use” in Section 58.1-3230 of the Code of Virginia and conducted by the owner of such real estate. 5601.2.4.2 Fireworks display. The permit holder shall furnish a bond or certificate of insurance in an amount deemed adequate by the legal department of the jurisdiction for the payment of all potential damages to a person or persons or to property by reason of the permitted display, and arising from any acts of the permit holder, the agent, employees or subcontractors, but in no case shall the value of the coverage be less than $1,000,000. | 5601.2.4 Financial responsibility. Before a permit is issued, as required by Section 5601.2, the applicant shall file with the jurisdiction a corporate surety bond in the principal sum of $500,000 or a public liability insurance policy for the same amount, for the purpose of the payment of all damages to persons or property which arise from, or are caused by, the conduct of any act authorized by the permit upon which any judicial judgment results. The legal department of the jurisdiction may specify a greater amount when conditions at the location of use indicate a greater amount is required. Government entities shall be exempt from this bond requirement. 5601.2.4.1 Blasting. Before approval to do blasting is issued, the applicant for approval shall file a bond or submit a certificate of insurance in such form, amount, and coverage as determined by the legal department of the jurisdiction to be adequate in each case to indemnify the jurisdiction against any and all damages arising from permitted blasting but in no case shall the value of the coverage be less than $1,000,000. Exception: Filing a bond or submitting a certificate of liability insurance is not required for blasting on real estate parcels of five or more acres conforming to the definition of "real estate devoted to agricultural use" or "real estate devoted to horticultural use" in § 58.1- 3230 of the Code of Virginia and conducted by the owner of such real estate. 5601.2.4.2 Fireworks display. The permit holder shall furnish a bond or certificate of insurance in an amount deemed adequate by the legal department of the jurisdiction for the payment of all potential damages to a person or persons or to property by reason of the permitted display, and arising from any acts of the permit holder, the agent, employees or subcontractors, but in no case shall the value of the coverage be less than $1,000,000.
5601.4 Qualifications. Persons in charge of magazines, blasting, fireworks display, or pyrotechnic special effect operations shall not be under the influence of alcohol or drugs which impair sensory or motor skills, shall be at least 21 years of age and possess knowledge of all safety precautions related to the storage, handling or use of explosives, explosive materials or fireworks. 5601.4.1 Certification of blasters and pyrotechnicians. Certificates as a restricted blaster, unrestricted blaster or pyrotechnician will be issued upon proof of successful completion of an examination approved by the SFMO commensurate to the certification sought and completion of a background investigation for compliance with § 27- 97.2 of the Code of Virginia. The applicant for certification shall submit proof to the SFMO of the following experience: 1. For certification as a restricted blaster, at least one year under direct supervision by a certified unrestricted blaster, certified restricted blaster or other person(s) approved by the SFMO. 2. For certification as an unrestricted blaster, at least one year under direct supervision by a certified unrestricted blaster or other person or persons approved by the SFMO. 3. For certification as a pyrotechnician, aerial, or pyrotechnician, proximate, applicant was in responsible charge of or has assisted in the documented design, setup and conducting of a fireworks display on at least six occasions within the 24 months immediately preceding the application for certification. The SFMO shall process all certification applicants for compliance with § 27-97.2 of the Code of Virginia and will be the sole provider of blaster and pyrotechnician certifications. Exception: The use of explosives by the owner of real estate parcels of five or more acres conforming to the definition of "real estate devoted to agricultural use" or "real estate devoted to horticultural use" in § 58.1-3230 of the Code of Virginia when blasting on such real estate.
5601.4.2 Certification issuance. The issuance of a certification as a blaster or pyrotechnician shall be denied if the applicant has (i) been convicted of any felony, whether such conviction occurred under the laws of the Commonwealth, or any other state, the District of Columbia, the United States or any territory thereof, unless his civil rights have been restored by the Governor or other appropriate authority, (ii) has not provided acceptable proof or evidence of the experience required in Section 5601.4.1, or (iii) has not provided acceptable proof or evidence of the continued training or education required in Section 5601.4.5. 5601.4.3 Fee for certification. The fee for obtaining or renewing a blaster or pyrotechnician certificate from the SFMO shall be $150 plus any additional fees charged by other agencies for fingerprinting and for obtaining a national criminal history record check through the Central Criminal Records Exchange to the Federal Bureau of Investigation. 5601.4.3.1 Fee for replacement certificate. A written request for a replacement blaster or pyrotechnician certificate shall be accompanied by the payment of an administrative fee in the amount of $20 made payable to the Treasurer of Virginia. Verbal requests shall not be accepted. | 5601.4.2 Certification issuance. The issuance of a certification as a blaster or pyrotechnician shall be denied if the applicant has (i) been convicted of any felony, whether such conviction occurred under the laws of the Commonwealth, or any other state, the District of Columbia, the United States or any territory thereof, unless his civil rights have been restored by the Governor or other appropriate authority, (ii) has not provided acceptable proof or evidence of the experience required in Section 5601.4.1, or (iii) has not provided acceptable proof or evidence of the continued training or education required in Section 5601.4.5. 5601.4.3 Fee for certification. The fee for obtaining or renewing a blaster or pyrotechnician certificate from the SFMO shall be $150 plus any additional fees charged by other agencies for fingerprinting and for obtaining a national criminal history record check through the Central Criminal Records Exchange to the Federal Bureau of Investigation. 5601.4.3.1 Fee for replacement certificate. A written request for a replacement blaster or pyrotechnician certificate shall be accompanied by the payment of an administrative fee in the amount of $20 made payable to the Treasurer of Virginia. Verbal requests shall not be accepted.
5601.4.4 Revocation of a blaster or pyrotechnician certification. After issuance of a blaster or pyrotechnician certification, subsequent conviction of a felony will be grounds for immediate revocation of a blaster or pyrotechnician certification, whether such conviction occurred under the laws of the Commonwealth, or any other state, the District of Columbia, the United States or any territory thereof. The certification shall be returned to the SFMO immediately. An individual may subsequently reapply for his blaster or pyrotechnician certification if his civil rights have been restored by the Governor or other appropriate authority. | 5601.4.4 Revocation of a blaster or pyrotechnician certification. After issuance of a blaster or pyrotechnician certification, subsequent conviction of a felony will be grounds for immediate revocation of a blaster or pyrotechnician certification, whether such conviction occurred under the laws of the Commonwealth, or any other state, the District of Columbia, the United States or any territory thereof. The certification shall be returned to the SFMO immediately. An individual may subsequently reapply for his blaster or pyrotechnician certification if his civil rights have been restored by the Governor or other appropriate authority.
5601.4.5 Expiration and renewal of a BCC, or blaster or pyrotechnician certification. A certificate for an unrestricted blaster, restricted blaster or pyrotechnician shall be valid for 3 years from the date of issuance. A BCC shall be valid for 3 years from the date of issuance. Renewal of the unrestricted blaster certificate will be issued upon proof of at least 16 accumulated hours of continued training or education in the use of explosives within 3 consecutive years and a background investigation for compliance with Section 27-97.2 of the Code of Virginia. Renewal of the restricted blaster certificate will be issued upon proof of at least 8 accumulated hours of continued training or education in the use of explosives within 3 consecutive years and a background investigation for compliance with Section 27-97.2 of the Code of Virginia. Renewal of the pyrotechnician certificate will be issued upon proof of at least 12 accumulated hours of continued training or education in the subject areas of explosives storage; the design, setup or conduct of a fireworks display within 3 consecutive years; and a background investigation for compliance with Section 27-97.2 of the Code of Virginia. The continued training or education required for renewal of a blaster or pyrotechnician certificate shall be obtained during the 3 years immediately prior to the certificate’s published expiration date. Failure to renew a blaster or pyrotechnician certificate in accordance with this section shall cause an individual to obtain another blaster or pyrotechnician certificate upon compliance with Section 5601.4.1 to continue engaging in the unsupervised use of explosives or conducting a fireworks display. | 5601.4.5 Expiration and renewal of a BCC, or blaster or pyrotechnician certification. A certificate for an unrestricted blaster, restricted blaster or pyrotechnician shall be valid for three years from the date of issuance. A BCC shall be valid for three years from the date of issuance. Renewal of the unrestricted blaster certificate will be issued upon proof of at least 16 accumulated hours of continued training or education in the use of explosives within three consecutive years and a background investigation for compliance with § 27-97.2 of the Code of Virginia. Renewal of the restricted blaster certificate will be issued upon proof of at least eight accumulated hours of continued training or education in the use of explosives within three consecutive years and a background investigation for compliance with § 27- 97.2 of the Code of Virginia. Renewal of the pyrotechnician certificate will be issued upon proof of at least 12 accumulated hours of continued training or education in the subject areas of explosives storage; the design, setup or conduct of a fireworks display within three consecutive years; and a background investigation for compliance with § 27-97.2 of the Code of Virginia. The continued training or education required for renewal of a blaster or pyrotechnician certificate shall be obtained during the three years immediately prior to the certificate's published expiration date. Failure to renew a blaster or pyrotechnician certificate in accordance with this section shall cause an individual to obtain another blaster or pyrotechnician certificate upon compliance with Section 5601.4.1 to continue engaging in the unsupervised use of explosives or conducting a fireworks display.
5601.4.6 Denial, suspension or revocation of a certificate. If issuance or renewal of a blaster or pyrotechnician certificate is denied, or upon the filing of a complaint against an applicant or certificate holder for non-performance, or performance in violation of the SFPC and the appropriate referenced NFPA 495, 1123 or 1126 standards, the State Fire Marshal may convene a three member panel to hear the particulars of the complaint or denial. The three member panel will be comprised of the following persons: 1.A Virginia certified fire official, excluding any person certified as a blaster or pyrotechnician, or who is on the staff of the SFMO. 2.A Virginia certified blaster or pyrotechnician whose certification is the same as that of the person to whom a complaint is lodged, and who is not associated in any way with the person against whom a complaint is lodged and whose work or employer is geographically remote, as much as practically possible, from the person to whom a complaint is lodged. 3.A member of the general public who does not have a vested financial interest in conducting a fireworks display, or the manufacture, sale, storage, or use of explosives. Upon the State Fire Marshal convening such panel, the hearing is to commence within 60 calendar days of the filing of the complaint or denial. The three member panel is to hear the complaint and render a written recommendation to the State Fire Marshal for certificate issuance, no action, revocation, or suspension of a certificate for a period not to exceed 6 months. Notwithstanding the discretionary decision and action to convene such panel, the State Fire Marshal reserves the authority to choose an action that may be contrary to the panel’s recommendation. A written decision of the State Fire Marshal is to be delivered to the party within 14 days of the hearing’s conclusion. If the certificate is denied, revoked or suspended by the SFMO, in accordance with Section 112.9, the party may file an appeal with the TRB. The party’s appeal to the TRB must be filed within 14 calendar days of the receipt of the State Fire Marshal’s written decision to deny, revoke, or suspend. The denial, revocation or suspension of a license is independent of any criminal proceedings that may be initiated by any state or local authority. 5601.4.6.1 Replacement of revoked certificate. Any person whose certificate as a pyrotechnician or blaster was revoked upon cause may apply for certification as a pyrotechnician or blaster 6 months or more from the date of the revocation and upon compliance with Section 5601.4.1. All elements of Section 5601.4.1 are required to be obtained and dated after the date of revocation. 5601.4.6.2 Return of suspended certificate. Any certificate that was suspended upon cause will be reinstated at the end of the suspension period without change to its expiration date. | 5601.4.6 Denial, suspension or revocation of a certificate. If issuance or renewal of a blaster or pyrotechnician certificate is denied, or upon the filing of a complaint against an applicant or certificate holder for non-performance, or performance in violation of the SFPC and the appropriate referenced NFPA 495, 1123 or 1126 standards, the State Fire Marshal may convene a threemember panel to hear the particulars of the complaint or denial. The threemember panel will be comprised of the following persons: 1. A Virginia certified fire official, excluding any person certified as a blaster or pyrotechnician, or who is on the staff of the SFMO. 2. A Virginia certified blaster or pyrotechnician whose certification is the same as that of the person to whom a complaint is lodged, and who is not associated in any way with the person against whom a complaint is lodged and whose work or employer is geographically remote, as much as practically possible, from the person to whom a complaint is lodged. 3. A member of the general public who does not have a vested financial interest in conducting a fireworks display, or the manufacture, sale, storage, or use of explosives. Upon the State Fire Marshal convening such panel, the hearing is to commence within 60 calendar days of the filing of the complaint or denial. The threemember panel is to hear the complaint and render a written recommendation to the State Fire Marshal for certificate issuance, no action, revocation, or suspension of a certificate for a period not to exceed six months. Notwithstanding the discretionary decision and action to convene such panel, the State Fire Marshal reserves the authority to choose an action that may be contrary to the panel's recommendation. A written decision of the State Fire Marshal is to be delivered to the party within 14 days of the hearing's conclusion. If the certificate is denied, revoked, or suspended by the SFMO, in accordance with Section 112.9, the party may file an appeal with the State Review Board. The party's appeal to State Review Board must be filed within 14 calendar days of the receipt of the State Fire Marshal's written decision to deny, revoke, or suspend. The denial, revocation, or suspension of a license is independent of any criminal proceedings that may be initiated by any state or local authority. 5601.4.6.1 Replacement of revoked certificate. Any person whose certificate as a pyrotechnician or blaster was revoked upon cause may apply for certification as a pyrotechnician or blaster six months or more from the date of the revocation and upon compliance with Section 5601.4.1. All elements of Section 5601.4.1 are required to be obtained and dated after the date of revocation. 5601.4.6.2 Return of suspended certificate. Any certificate that was suspended upon cause will be reinstated at the end of the suspension period without change to its expiration date
5601.7 Seizure. The fire official is authorized to remove or cause to be removed or disposed of in an approved manner, at the expense of the owner, fireworks offered or exposed for sale, stored, possessed or used in violation of this chapter. | 5601.7 Seizure. The fire official is authorized to remove or cause to be removed or disposed of in an approved manner, at the expense of the owner, fireworks offered or exposed for sale, stored, possessed or used in violation of this chapter.
5601.8.1.1 Mass-detonating explosives (Division 1.1, 1.2 or 1.5). The total net explosive weight of mass-detonating explosives (Division 1.1, 1.2 or 1.5) shall be used. See Table 5604.5.2(1) or Table 5605.3 as appropriate. Exception: When the TNT equivalence of the explosive material has been determined, the equivalence is allowed to be used to establish the net explosive weight. | 5601.8.1.1 Mass-detonating explosives (Division 1.1, 1.2 or 1.5). The total net explosive weight of mass-detonating explosives (Division 1.1, 1.2 or 1.5) shall be used. See Table 5604.5.2(1) as appropriate. Exception: Where the TNT equivalence of the explosive material has been determined, the equivalence is allowed to be used to establish the net explosive weight.
5601.8.1.3 Combinations of mass-detonating and nonmass-detonating explosives (excluding Division 1.4). Combination of mass-detonating and nonmass-detonating explosives (excluding Division 1.4) shall be as follows: 1.When Division 1.1 and 1.2 explosives are located in the same site, determine the distance for the total quantity considered first as 1.1 and then as 1.2. The required distance is the greater of the two. When the Division 1.1 requirements are controlling and the TNT equivalence of the 1.2 is known, the TNT equivalent weight of the 1.2 items shall be allowed to be added to the total explosive weight of Division 1.1 items to determine the net explosive weight for Division 1.1 distance determination. See Table 5604.5.2(2) or Table 5605.3 as appropriate. 2.When Division 1.1 and 1.3 explosives are located in the same site, determine the distances for the total quantity considered first as 1.1 and then as 1.3. The required distance is the greater of the two. When the Division 1.1 requirements are controlling and the TNT equivalence of the 1.3 is known, the TNT equivalent weight of the 1.3 items shall be allowed to be added to the total explosive weight of Division 1.1 items to determine the net explosive weight for Division 1.1 distance determination. See Table 5604.5.2(1), 5604.5.2(2) or 5605.3, as appropriate. 3.When Division 1.1, 1.2 and 1.3 explosives are located in the same site, determine the distances for the total quantity considered first as 1.1, next as 1.2 and finally as 1.3. The required distance is the greatest of the three. As allowed by paragraphs 1 and 2 above, TNT equivalent weights for 1.2 and 1.3 items are allowed to be used to determine the net weight of explosives for Division 1.1 distance determination. Table 5604.5.2(1) or 5605.3 shall be used when TNT equivalency is used to establish the net explosive weight. 4.For composite pyrotechnic items Division 1.1 and Division 1.3, the sum of the net weights of the pyrotechnic composition and the explosives involved shall be used. See Tables 5604.5.2(1) and 5604.5.2(2). | 5601.8.1.3 Combinations of massdetonating and non-mass-detonating explosives (excluding Division 1.4). Combination of mass-detonating and nonmass-detonating explosives (excluding Division 1.4) shall be as follows: 1. Where Divisions 1.1 and 1.2 explosives are located in the same site, determine the distance for the total quantity considered first as Division 1.1 and then as Division 1.2. The required distance is the greater of the two. Where the Division 1.1 requirements are controlling and the TNT equivalence of the Division 1.2 is known, the TNT equivalent weight of the Division 1.2 items shall be allowed to be added to the total explosive weight of Division 1.1 items to determine the net explosive weight for Division 1.1 distance determination. See Table 5604.5.2(2) as appropriate. 2. Where Divisions 1.1 and 1.3 explosives are located in the same site, determine the distances for the total quantity considered first as Division 1.1 and then as Division 1.3. The required distance is the greater of the two. Where the Division 1.1 requirements are controlling and the TNT equivalence of the Division 1.3 is known, the TNT equivalent weight of the Division 1.3 items shall be allowed to be added to the total explosive weight of Division 1.1 items to determine the net explosive weight for Division 1.1 distance determination. See Table 5604.5.2(1) or Table 5604.5.2(2) as appropriate. 3. Where Divisions 1.1, 1.2 and 1.3 explosives are located in the same site, determine the distances for the total quantity considered first as Division 1.1, next as Division 1.2 and finally as Division 1.3. The required distance is the greatest of the three. As allowed by subdivisions 1 and 2 of this subsection, TNT equivalent weights for Division 1.2 and Division 1.3 items are allowed to be used to determine the net weight of explosives for Division 1.1 distance determination. Table 5604.5.2(1) shall be used where TNT equivalency is used to establish the net explosive weight. 4. For composite pyrotechnic items Division 1.1 and Division 1.3, the sum of the net weights of the pyrotechnic composition and the explosives involved shall be used. See Tables 5604.5.2(1) and 5604.5.2(2).
5605.6.4.1 Magazines. Magazines used for storage in processing areas shall be in accordance with the requirements of Section 5604.5.1. All explosive materials shall be removed to appropriate storage magazines for unattended storage at the end of the work day. The contents of indoor magazines shall be added to the quantity of explosives contained at individual workstations and the total quantity of material stored, processed or used shall be utilized to establish the intraplant separation distances indicated by Table 5605.3 or 5604.5.2(3), as appropriate. | 5605.6.4.1 Magazines. Magazines used for storage in processing areas shall be in accordance with the requirements of Section 5604.5.1. Explosive materials shall be removed to appropriate storage magazines for unattended storage at the end of the work day. The contents of indoor magazines shall be added to the quantity of explosives contained at individual workstations and the total quantity of material stored, processed or used shall be utilized to establish the intraplant separation distances indicated by Table 5604.5.2(3) as appropriate.
5606.5.2.1 Smokeless propellant. Commercial stocks of smokeless propellants shall be stored as follows: 1.Quantities exceeding 20 pounds (9 kg), but not exceeding 100 pounds (45 kg) shall be stored in portable wooden boxes having walls of at least 1 inch (25 mm) nominal thickness or equivalent. 2.Quantities exceeding 100 pounds (45 kg), but not exceeding 800 pounds (363 kg), shall be stored in storage cabinets having walls at least 1 inch (25 mm) nominal thickness or equivalent. Not more than 400 pounds (182 kg) shall be stored in any one cabinet, and cabinets shall be separated by a distance of at least 25 feet (7620 mm) or by a fire partition having a fire-resistance rating of at least 1 hour. 3.Storage of quantities exceeding 800 pounds (363 kg), but not exceeding 5,000 pounds (2270 kg) in a building shall comply with all of the following: 3.1.The storage is inaccessible to unauthorized personnel. 3.2.Smokeless propellant shall be stored in nonportable storage cabinets having wood walls at least 1 inch (25 mm) nominal thickness or equivalent and having shelves with no more than 3 feet (914 mm) of vertical separation between shelves. 3.3.No more than 400 pounds (182 kg) is stored in any one cabinet. 3.4.Cabinets shall be located against walls with at least 40 feet (12 192 mm) between cabinets. The minimum required separation between cabinets may be reduced to 20 feet (6096 mm) provided that barricades twice the height of the cabinets are attached to the wall, midway between each cabinet. The barricades must extend a minimum of 10 feet (3048 mm) outward, be firmly attached to the wall, and be constructed of steel not less than 0.25 inch thick (6.4 mm), 2-inch (51 mm) nominal thickness wood, brick, or concrete block. 3.5.Smokeless propellant shall be separated from materials classified as combustible liquids, flammable liquids, flammable solids, or oxidizing materials by a distance of 25 feet (7620 mm) or by a fire partition having a fire-resistance rating of 1 hour. 3.6.The building shall be equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. 4.Smokeless propellants not stored according to Item 1, 2, or 3 above shall be stored in a Type 2 or 4 magazine in accordance with Section 3304 and NFPA 495. | 5606.5.2.1 Smokeless propellant. Commercial stocks of smokeless propellants shall be stored as follows: 1. Quantities exceeding 20 pounds (9 kg), but not exceeding 100 pounds (45 kg) shall be stored in portable wooden boxes having walls of not less than 1 inch (25 mm) nominal thickness or equivalent. 2. Quantities exceeding 100 pounds (45 kg), but not exceeding 800 pounds (363 kg), shall be stored in storage cabinets having walls not less than 1 inch (25 mm) nominal thickness or equivalent. Not more than 400 pounds (182 kg) shall be stored in any one cabinet, and cabinets shall be separated by a distance of at least 25 feet (7620 mm) or by a fire partition having a fire-resistance rating of at least 1 hour. 3. Storage of quantities exceeding 800 pounds (363 kg), but not exceeding 5,000 pounds (2270 kg) in a building shall comply with all of the following: 3.1. The storage is inaccessible to unauthorized personnel. 3.2. Smokeless propellant shall be stored in nonportable storage cabinets having wood walls not less than 1 inch (25 mm) nominal thickness or equivalent and having shelves with not no more than 3 feet (914 mm) of vertical separation between shelves. 3.3. No more than 400 pounds (182 kg) is stored in any one cabinet. 3.4. Cabinets shall be located against walls with at least 40 feet (12 192 mm) between cabinets. 3.5. The minimum required separation between cabinets may be reduced to 20 feet (6096 mm) provided that barricades twice the height of the cabinets are attached to the wall, midway between each cabinet. The barricades must extend a minimum of 10 feet (3048 mm) outward, be firmly attached to the wall and be constructed of steel not less than 1/4 inch thick (6.4 mm), 2-inch (51 mm) nominal thickness wood, brick or concrete block. 3.6. Smokeless propellant shall be separated from materials classified as combustible liquids, flammable liquids, flammable solids or oxidizing materials by a distance of 25 feet (7620 mm) or by a fire partition having a fireresistance rating of 1 hour. 3.7. The building shall be equipped throughout with an automatic sprinkler system installed in accordance with the applicable building code. 4. Smokeless propellants not stored in according to Item 1, 2, or 3 shall be stored in a Type 2 or 4 magazine in accordance with Section 5604 and NFPA 495.
5606.5.2.3 Small arms primers. Commercial stocks of small arms primers shall be stored as follows: 1.Quantities not to exceed 750,000 small arms primers stored in a building shall be arranged such that not more than 100,000 small arms primers are stored in any one pile and piles are at least 15 feet (4572 mm) apart. 2.Quantities exceeding 750,000 small arms primers stored in a building shall comply with all of the following: 2.1.The warehouse or storage building shall not be accessible to unauthorized personnel. 2.2.Small arms primers shall be stored in cabinets. No more than 200,000 small arms primers shall be stored in any one cabinet. 2.3.Shelves in cabinets shall have vertical separation of at least 2 feet (610 mm). 2.4.Cabinets shall be located against walls of the warehouse or storage room with at least 40 feet (12 192 mm) between cabinets. The minimum required separation between cabinets shall be allowed to be reduced to 20 feet (6096 mm) provided that barricades twice the height of the cabinets are attached to the wall, midway between each cabinet. The barricades shall be firmly attached to the wall and shall be constructed of steel not less than 1/4 inch thick (6.4 mm), 2-inch (51 mm) nominal thickness wood, brick or concrete block. 2.5.Small arms primers shall be separated from materials classified as combustible liquids, flammable liquids, flammable solids or oxidizing materials by a distance of 25 feet (7620 mm) by a fire partition having a fire-resistance rating of 1 hour. 2.6.The building shall be protected throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. 3.Small arms primers not stored in accordance with Item 1 or 2 of this section shall be stored in a magazine meeting the requirements of Section 5604 and NFPA 495. | 5606.5.2.3 Small arms primers. Commercial stocks of small arms primers shall be stored as follows: 1. Quantities not to exceed 750,000 small arms primers stored in a building shall be arranged such that not more than 100,000 small arms primers are stored in any one pile and piles are not less than 15 feet (4572 mm) apart. 2. Quantities exceeding 750,000 small arms primers stored in a building shall comply with all of the following: 2.1. The warehouse or storage building shall not be accessible to unauthorized personnel. 2.2. Small arms primers shall be stored in cabinets. Not more than 200,000 small arms primers shall be stored in any one cabinet. 2.3. Shelves in cabinets shall have vertical separation of not less than 2 feet (610 mm). 2.4. Cabinets shall be located against walls of the warehouse or storage room with not less than 40 feet (12 192 mm) between cabinets. The minimum required separation between cabinets shall be allowed to be reduced to 20 feet (6096 mm) provided that barricades twice the height of the cabinets are attached to the wall, midway between each cabinet. The barricades shall be firmly attached to the wall and shall be constructed of steel not less than 1/4 inch thick (6.4 mm), 2-inch (51 mm) nominal thickness wood, brick or concrete block. 2.5. Small arms primers shall be separated from materials classified as combustible liquids, flammable liquids, flammable solids or oxidizing materials by a distance of 25 feet (7620 mm) by a fire partition having a fireresistance rating of 1 hour. 2.6. The building shall be protected throughout with an automatic sprinkler system installed in accordance with the applicable building code. 3. Small arms primers not stored in accordance with Item 1 or 2 of this section shall be stored in a magazine meeting the requirements of Section 5604 and NFPA 495.
Same | Add the following to the list of definitions in Section 5602.1: Background clearance card (BCC). Blaster, restricted. Blaster, unrestricted. Design. Designated individual. Fireworks. Fireworks, 1.4G. Fireworks, 1.3G. Permissible fireworks. Pyrotechnician (fireworks operator). Pyrotechnician, aerial. Pyrotechnician, proximate. Responsible management. Smokeless propellants. Sole proprietor.
5603.4 Accidents. Accidents involving the use of explosives, explosive materials and fireworks, which result in injuries or property damage, shall be immediately reported by the permit holder to the fire code official and State Fire Marshal. | 5603.4 Accidents. Accidents involving the use of explosives, explosive materials, and fireworks, which result in injuries or property damage, shall be immediately reported by the permit holder to the fire code official and State Fire Marshal.
5605.1 General. The manufacture, assembly and testing of explosives, ammunition, blasting agents and fireworks shall comply with the requirements of this section, Title 59.1, Chapter 11 of the Code of Virginia, and NFPA 495 or NFPA 1124. Exceptions: 1.The hand loading of small arms ammunition prepared for personal use and not offered for resale. 2.The mixing and loading of blasting agents at blasting sites in accordance with NFPA 495. 3.The use of binary explosives or plosophoric materials in blasting or pyrotechnic special effects applications in accordance with NFPA 495 or NFPA 1126. | 5605.1 General. The restricted and unrestricted manufacture, assembly and testing of explosives, ammunition, blasting agents and fireworks shall comply with the requirements of this section, NFPA 495, NFPA 1124, or NFPA 1126. Exceptions: 1. The hand loading of small arms ammunition prepared for personal use and not offered for resale. 2. The mixing and loading of blasting agents at blasting sites in accordance with NFPA 495.
5605.1.1 Permits. Permits for the manufacture, assembly and testing of explosives, ammunition, blasting agents and fireworks shall be required as set forth in Section 107.2 and regulated in accordance with this section. A permit to manufacture any explosive material in any quantity shall be prohibited unless such manufacture is authorized by a federal license and conducted in accordance with recognized safety practices. | 5605.1.1 Permits. Permits for the restricted and unrestricted explosives manufacture, assembly and testing of explosives, ammunition, blasting agents and fireworks shall be required as set forth in Section 107.2 and regulated in accordance with this section. A permit for unrestricted explosives manufacturing of any explosive material shall be prohibited unless such manufacture is authorized by a federal license and conducted in accordance with recognized safety practices. All restricted explosives manufacturing shall comply with the instructions provided by the supplier of the components used in the manufacture of the explosive material. Exceptions: 1. Any recreational use of reactive targets is not required to obtain a permit for restricted explosives manufacture or explosives use when such manufacture and use complies with all of the following: 1.1. The manufacture and use is limited to one pound or less per unit on private property with the permission of the property owner and used no closer than 500 feet from a roadway or structure; 1.2. The manufacture of the reactive target complies with the instructions provided by the producer of the components used in the manufacture; 1.3. The reactive target manufactured is for immediate use without any residual storage or transportation; and 1.4. The exploding or use of the target is in conformance with its intended purpose by the manufacturer of the reactive target and does not involve the deliberate destruction of any property, vehicle, structure or animal life. 2. The owner of real estate parcels of five or more acres conforming to the definition of "real estate devoted to agricultural use" or "real estate devoted to horticultural use" in § 58.1-3230 of the Code of Virginia is not required to obtain a permit for restricted explosives manufacture when such manufacture complies with all of the following: 2.1. The manufacture of the explosives is conducted by the owner of such real estate; 2.2. The manufacture of the explosives complies with the instructions provided by the producer of the components used in the manufacture; 2.3. The explosive used does not include reactive targets; 2.4. The reactive target manufactured is for immediate use without any residual storage or transportation; and 2.5. A permit to use explosives has been obtained in accordance with Section 107.2. 3. An applicant that is performing nonpersonal, business work is not required to obtain a permit for restricted explosives manufacture when such manufacture complies with all of the following: 3.1. The applicant's certified blaster who manufactures the explosives complies with the instructions provided by the producer of the components used in the manufacture; 3.2. The explosive used does not include the use of reactive targets; 3.3. The explosive material manufactured is for immediate use without any residual storage or transportation; and 3.4. A permit to use explosives has been obtained in accordance with Section 107.2.
5605.3 Intraplant separation of operating buildings. Explosives manufacturing buildings and fireworks manufacturing buildings, including those where explosive charges are assembled, manufactured, prepared or loaded utilizing Division 1.1, 1.2, 1.3, 1.4 or 1.5 explosives, shall be separated from all other buildings, including magazines, within the confines of the manufacturing plant, at a distance not less than those shown in Table 5605.3 or 5604.5.2(3), as appropriate. Exception: Fireworks manufacturing buildings separated in accordance with NFPA 1124. The quantity of explosives in an operating building shall be the net weight of all explosives contained therein. Distances shall be based on the hazard division requiring the greatest separation, unless the aggregate explosive weight is divided by approved walls or shields designed for that purpose. When dividing a quantity of explosives into smaller stacks, a suitable barrier or adequate separation distance shall be provided to prevent propagation from one stack to another. When distance is used as the sole means of separation within a building, such distance shall be established by testing. Testing shall demonstrate that propagation between stacks will not result. Barriers provided to protect against explosive effects shall be designed and installed in accordance with approved standards. | (N)5605.3 Intraplant separation of operating buildings. (Section deleted)
TABLE 5605.3 MINIMUM INTRALINE (INTRAPLANT) SEPARATION DISTANCES (ILD OR IPD) BETWEEN BARRICADED OPERATING BUILDINGS CONTAINING EXPLOSIVES—DIVISION 1.1, 1.2 OR 1.5 MASS-EXPLOSION HAZARDa | (N)TABLE 5605.3 MINIMUM INTRALINE (INTRAPLANT) SEPARATION DISTANCES (ILD OR IPD) BETWEEN BARRICADED OPERATING BUILDINGS CONTAINING EXPLOSIVES—DIVISION 1.1, 1.2 OR 1.5 MASS-EXPLOSION HAZARD (Table deleted)
5605.4 Separation of manufacturing operating buildings from inhabited buildings, public traffic routes and magazines. When an operating building on an explosive materials plant site is designed to contain explosive materials, such a building shall be located away from inhabited buildings, public traffic routes and magazines in accordance with Table 5604.5.2(2) or 5604.5.2(3) as appropriate, based on the maximum quantity of explosive materials permitted to be in the building at one time (see Section 5601.8). Exception: Fireworks manufacturing buildings constructed and operated in accordance with NFPA 1124. | (N)5605.4 Separation of manufacturing operating buildings from inhabited buildings, public traffic routes and magazines. Where an operating building on an explosive materials plant site is designed to contain explosive materials, such a building shall be maintained in accordance with the applicable building code.
5605.5 Buildings and equipment. Buildings or rooms that exceed the maximum allowable quantity per control area of explosive materials shall be operated in accordance with this section and constructed in accordance with the requirements of the International Building Code for Group H occupancies. Exception: Fireworks manufacturing buildings constructed and operated in accordance with NFPA 1124. | (N)5605.5 Buildings and equipment. Buildings or rooms that exceed the maximum allowable quantity per control area of explosive materials shall be operated in accordance with this section. Exception: Fireworks manufacturing buildings constructed and operated in accordance with NFPA 1124.
5605.6.4 Quantity limits. The quantity of explosives at any particular work station shall be limited to that posted on the load limit signs for the individual work station. The total quantity of explosives for multiple workstations shall not exceed that established by the intraplant distances in Table 5605.3 or 5604.5.2(3), as appropriate. | (N)5605.6.4 Quantity limits. The quantity of explosives at any particular work station shall be limited to that posted on the load limit signs for the individual work station. The total quantity of explosives for multiple workstations shall not exceed that established by the intraplant distances in accordance with the applicable building code.
5606.4 Storage in residences. Propellants for personal use in quantities not exceeding 50 pounds (23 kg) of black powder or 100 pounds (45 kg) of smokeless powder shall be stored in original containers in occupancies limited to Groups R-3 and R-5, or 200 pounds (91 kg) of smokeless powder when stored in the manufacturer’s original containers in detached Group U structures that are at least 10 feet (3048 m) from inhabited buildings and are accessory to Group R-3 or R-5. In other than Group R-3 or R-5, smokeless powder in quantities exceeding 20 pounds (9 kg) but not exceeding 50 pounds (23 kg) shall be kept in a wooden box or cabinet having walls of at least 1 inch (25 mm) nominal thickness or equivalent. | 5606.4 Storage in residences. Propellants for personal use in quantities not exceeding 50 pounds (23 kg) of black powder or 100 pounds (45 kg) of smokeless powder shall be stored in original containers in occupancies limited to Groups R-3 and R-5, or 200 pounds (91 kg) of smokeless powder when stored in the manufacturer's original containers in detached Group U structures that are at least 10 feet from inhabited buildings and are accessory to Group R-3 or R-5. In other than Group R-3 or R-5, smokeless powder in quantities exceeding 20 pounds (9 kg) but not exceeding 50 pounds (23 kg) shall be kept in a wooden box or cabinet having walls of at least one inch (25 mm) nominal thickness or equivalent.
5606.4.1 Black powder. (Section deleted.) 5606.4.2 Smokeless propellants. (Section deleted.) 5606.4.3 Small arms primers. (Section deleted.) | (N)5606.4.1 Black powder. (Section deleted) (N)5606.4.2 Smokeless propellants. (Section deleted) (N)5606.4.3 Small arms primers. (Section deleted)
5606.5.1.1 Smokeless propellant. No more than 100 pounds (45 kg) of smokeless propellants, in containers of 8 pounds (3.6 kg) or less capacity, shall be displayed in Group M occupancies. | 5606.5.1.1 Smokeless propellant. No more than 100 pounds (45 kg) of smokeless propellants, in containers of 8 pounds (3.6 kg) or less capacity, shall be displayed in Group M occupancies.
5606.5.1.3 Small arms primers. (Section deleted.) | (N)5606.5.1.3 Small arms primers. (Section deleted)
5606.5.2.1 Smokeless propellant. Commercial stocks of smokeless propellants shall be stored as follows: 1.Quantities exceeding 20 pounds (9 kg), but not exceeding 100 pounds (45 kg) shall be stored in portable wooden boxes having walls of at least 1 inch (25 mm) nominal thickness or equivalent. 2.Quantities exceeding 100 pounds (45 kg), but not exceeding 800 pounds (363 kg), shall be stored in storage cabinets having walls at least 1 inch (25 mm) nominal thickness or equivalent. Not more than 400 pounds (182 kg) shall be stored in any one cabinet, and cabinets shall be separated by a distance of at least 25 feet (7620 mm) or by a fire partition having a fire-resistance rating of at least 1 hour. 3.Storage of quantities exceeding 800 pounds (363 kg), but not exceeding 5,000 pounds (2270 kg) in a building shall comply with all of the following: 3.1.The storage is inaccessible to unauthorized personnel. 3.2.Smokeless propellant shall be stored in nonportable storage cabinets having wood walls at least 1 inch (25 mm) nominal thickness or equivalent and having shelves with no more than 3 feet (914 mm) of vertical separation between shelves. 3.3.No more than 400 pounds (182 kg) is stored in any one cabinet. 3.4.Cabinets shall be located against walls with at least 40 feet (12 192 mm) between cabinets. The minimum required separation between cabinets may be reduced to 20 feet (6096 mm) provided that barricades twice the height of the cabinets are attached to the wall, midway between each cabinet. The barricades must extend a minimum of 10 feet (3048 mm) outward, be firmly attached to the wall, and be constructed of steel not less than 0.25 inch thick (6.4 mm), 2-inch (51 mm) nominal thickness wood, brick, or concrete block. 3.5.Smokeless propellant shall be separated from materials classified as combustible liquids, flammable liquids, flammable solids, or oxidizing materials by a distance of 25 feet (7620 mm) or by a fire partition having a fire-resistance rating of 1 hour. 3.6.The building shall be equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. 4.Smokeless propellants not stored according to Item 1, 2, or 3 above shall be stored in a Type 2 or 4 magazine in accordance with Section 3304 and NFPA 495. | 5606.5.2.1 Smokeless propellant. Commercial stocks of smokeless propellants shall be stored as follows: 1. Quantities exceeding 20 pounds (9 kg), but not exceeding 100 pounds (45 kg) shall be stored in portable wooden boxes having walls of at least one inch (25 mm) nominal thickness or equivalent. 2. Quantities exceeding 100 pounds (45 kg), but not exceeding 800 pounds (363 kg), shall be stored in storage cabinets having walls at least one inch (25 mm) nominal thickness or equivalent. Not more than 400 pounds (182 kg) shall be stored in any one cabinet, and cabinets shall be separated by a distance of at least 25 feet (7620 mm) or by a fire partition having a fire-resistance rating of at least one hour. 3. Storage of quantities exceeding 800 pounds (363 kg), but not exceeding 5,000 pounds (2270 kg) in a building shall comply with all of the following: 3.1. The storage is inaccessible to unauthorized personnel. 3.2. Smokeless propellant shall be stored in nonportable storage cabinets having wood walls at least one inch (25 mm) nominal thickness or equivalent and having shelves with no more than three feet (914 mm) of vertical separation between shelves. 3.3. No more than 400 pounds (182 kg) is stored in any one cabinet. 3.4. Cabinets shall be located against walls with at least 40 feet (12 192 mm) between cabinets. The minimum required separation between cabinets may be reduced to 20 feet (6096 mm) provided that barricades twice the height of the cabinets are attached to the wall, midway between each cabinet. The barricades must extend a minimum of 10 feet (3048 mm) outward, be firmly attached to the wall, and be constructed of steel not less than 0.25 inch thick (6.4 mm), two-inch (51 mm) nominal thickness wood, brick, or concrete block. 3.5. Smokeless propellant shall be separated from materials classified as combustible liquids, flammable liquids, flammable solids, or oxidizing materials by a distance of 25 feet (7620 mm) or by a fire partition having a fireresistance rating of one hour. 3.6. The building shall be equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. 4. Smokeless propellants not stored according to Item 1, 2, or 3 above shall be stored in a Type 2 or 4 magazine in accordance with Section 5604 and NFPA 495.
5607.1 General. Blasting operations shall be conducted only by persons certified by the SFMO as a restricted or unrestricted blaster or shall be supervised on-site by a person properly certified by the SFMO as a restricted or unrestricted blaster. | 5607.1 General. Blasting operations shall be conducted only by persons certified by the SFMO as a restricted or unrestricted blaster or shall be supervised on-site by a person properly certified by the SFMO as a restricted or unrestricted blaster.
5607.16 Blast records. A record of each blast shall be kept and retained for at least 5 years and shall be readily available for inspection by the code official. The record shall be in a format selected by the blaster and shall contain the minimum data and information indicated in Form 5607.16. | 5607.16 Blast records. A record of each blast shall be kept and retained for at least five years and shall be readily available for inspection by the code official. The record shall be in a format selected by the blaster and shall contain the minimum data and information indicated in Form 5607.16.
5608.2 Permit application. Prior to issuing permits for a fireworks display, plans for the fireworks display, inspections of the display site and demonstrations of the display operations shall be approved. A plan establishing procedures to follow and actions to be taken in the event that a shell fails to ignite in, or discharge from, a mortar or fails to function over the fallout area or other malfunctions shall be provided to the fire code official. In addition to the requirements of Section 5601.2.3.1, a permit to conduct a fireworks display shall not be issued to any applicant without the applicant identifying on the application the pyrotechnician who will be in responsible charge of the fireworks display and who is appropriately certified as a pyrotechnician in accordance with Section 5601.4.1. Exception: Permits are not required for the use or display of permissible fireworks on private property with the consent of the owner of such property. | 5608.2 Permit application. Prior to issuing permits for a fireworks display, plans for the fireworks display, inspections of the display site and demonstrations of the display operations shall be approved. A plan establishing procedures to follow and actions to be taken in the event that a shell fails to ignite in, or discharge from, a mortar or fails to function over the fallout area or other malfunctions shall be provided to the fire code official. In addition to the requirements of Section 5601.2.3.1, a permit to conduct a fireworks display shall not be issued to any applicant without the applicant identifying on the application the pyrotechnician who will be in responsible charge of the fireworks display and who is appropriately certified as a pyrotechnician in accordance with Section 5601.4.1. Exception: Permits are not required for the use or display of permissible fireworks on private property with the consent of the owner of such property.
5608.3 Approved fireworks displays. Approved fireworks displays shall include only the approved fireworks 1.3G, fireworks 1.4G, fireworks 1.4S and pyrotechnic articles 1.4G. The design, setup, conducting or direct on-site supervision of the design, setup and conducting of any fireworks display, either inside a building or outdoors, shall be performed only by persons certified by the SFMO in accordance with Section 5601.4.1 as a pyrotechnician (firework operator) and at least one person properly certified by the SFMO as a pyrotechnician shall be present at the site where the fireworks display is being conducted. The approved fireworks shall be arranged, located, discharged and fired in a manner that will not pose a hazard to property or endanger any person. Exception: Certification as a pyrotechnician is not required for the use or display of permissible fireworks when conducted on private property with the consent of the owner of such property. | 5608.3 Approved fireworks displays. Approved fireworks displays shall include only the approved fireworks 1.3G, fireworks 1.4G, fireworks 1.4S and pyrotechnic articles 1.4G. The design, setup, conducting or direct on-site supervision of the design, setup and conducting of any fireworks display, either inside a building or outdoors, shall be performed only by persons certified by the SFMO in accordance with Section 5601.4.1 as a pyrotechnician (firework operator) and at least one person properly certified by the SFMO as a pyrotechnician shall be present at the site where the fireworks display is being conducted. The approved fireworks shall be arranged, located, discharged and fired in a manner that will not pose a hazard to property or endanger any person. Exception: Certification as a pyrotechnician is not required for the use or display of permissible fireworks when conducted on private property with the consent of the owner of such property.
5608.4 Clearance. Spectators, spectator parking areas, and dwellings, buildings or structures shall not be located within the display site. The site for the outdoor land or water display shall have at least 100 feet-per-inch (31 m/2.4 mm) radius of internal mortar diameter of the largest shell to be fired as shown in Table 5608.4. Exceptions: 1.This provision shall not apply to pyrotechnic special effects and fireworks displays using Division 1.4G materials before a proximate audience in accordance with NFPA 1126. 2.This provision shall not apply to unoccupied dwellings, buildings and structures with the approval of the building owner and the fire code official. | 5608.4 Clearance. Spectators, spectator parking areas, and dwellings, buildings or structures shall not be located within the display site. The site for the outdoor land or water display shall have at least 100-ft/in. (31-m/2.4mm) radius of internal mortar diameter of the largest shell to be fired as shown in Table 5608.4. Exceptions: 1. This provision shall not apply to pyrotechnic special effects and fireworks displays using Division 1.4G materials before a proximate audience in accordance with NFPA 1126. 2. This provision shall not apply to unoccupied dwellings, buildings and structures with the approval of the building owner and the fire code official.
5608.4.1 Non-splitting, non-bursting comets and mines. For non-splitting or non-bursting comets and mines containing only stars or non-splitting or non-bursting comets, the minimum required radius of the display site shall be 50 feet per inch (15.24 m per 25.4 mm) of the internal mortar diameter of the largest comet or mine to be fired, one-half that shown in Table 5608.4. | 5608.4.1 Non-splitting, non-bursting comets and mines. For non-splitting or nonbursting comets and mines containing only stars or non-splitting or non-bursting comets, the minimum required radius of the display site shall be 50 feet per inch (15.24 m per 25.4 mm) of the internal mortar diameter of the largest comet or mine to be fired, one-half that shown in Table 5608.4.
5608.4.2 Special distance requirements. The minimum distance requirements of Table 5608.4 shall be adjusted as follows: 1.For chain-fused aerial shells and comets and mines to be fired from mortars, racks, or other holders that are sufficiently strong to prevent their being repositioned in the event of an explosive malfunction of the aerial shells, comets, or mines, the minimum required radius shall be the same as that required in Sections 5608.4 and 5608.4.1. For chain-fused aerial shells and comets and mines to be fired from mortars, racks, or other holders that are not sufficiently strong to prevent their being repositioned in the event of an explosive malfunction of the aerial shells, comets, or mines, or if there is doubt concerning the strength of racks holding chain-fused mortars, based upon the largest mortar in the sequence, the minimum required radius shall be double that required in Sections 5608.4 and 5608.4.1. 2.Distances from the point of discharge of any firework to a health care or detention and correctional facility, or the bulk storage of materials that have flammability, explosive, or toxic hazard shall be at least twice the distances specified in Table 5608.4. 3.The minimum required spectator separation distance for roman candles and cakes that produce aerial shells, comets, or mine effects shall be the same as the minimum required radius specified in Table 5608.4. 4.Aerial shells, comets and mines, and roman candles and cakes shall be permitted to be angled if the dud shells or components are carried away from the main spectator area and either of the following requirements is satisfied: 4.1.The offset specified in Table 5608.4 is followed. 4.2.The separation distance is correspondingly increased in the direction of the angle. If the offset provided in Table 5608.4 is followed, the mortars or tubes shall be angled so that any dud shells or components fall at a point approximately equal to the offset of the mortars or tubes from the otherwise required discharge point but in the opposite direction. | 5608.4.2 Special distance requirements. The minimum distance requirements of Table 5608.4 shall be adjusted as follows: 1. For chain-fused aerial shells and comets and mines to be fired from mortars, racks, or other holders that are sufficiently strong to prevent their being repositioned in the event of an explosive malfunction of the aerial shells, comets, or mines, the minimum required radius shall be the same as that required in Sections 5608.4 and 5608.4.1. For chain fused aerial shells and comets and mines to be fired from mortars, racks, or other holders that are not sufficiently strong to prevent their being repositioned in the event of an explosive malfunction of the aerial shells, comets, or mines, or if there is doubt concerning the strength of racks holding chain-fused mortars, based upon the largest mortar in the sequence, the minimum required radius shall be double that required in Sections 5608.4 and 5608.4.1. 2. Distances from the point of discharge of any firework to a health care or detention and correctional facility, or the bulk storage of materials that have flammability, explosive, or toxic hazard shall be at least twice the distances specified in Table 5608.4. 3. The minimum required spectator separation distance for roman candles and cakes that produce aerial shells, comets, or mine effects shall be the same as the minimum required radius specified in Table 5608.4. 4. Aerial shells, comets and mines, and roman candles and cakes shall be permitted to be angled if the dud shells or components are carried away from the main spectator area and either of the following requirements is satisfied: 4.1. The offset specified in Table 5608.4 is followed. 4.2. The separation distance is correspondingly increased in the direction of the angle. If the offset provided in Table 5608.4 is followed, the mortars or tubes shall be angled so that any dud shells or components fall at a point approximately equal to the offset of the mortars or tubes from the otherwise required discharge point but in the opposite direction.
TABLE 5608.4 DISTANCES FOR OUTDOOR FIREWORKS DISPLAY SITES: MINIMUM SEPARATION DISTANCES FROM MORTARS TO SPECTATORS FOR LAND AND WATER DISPLAYS | Add Table 5608.4 to read:

## Ch57 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
5701.1.1Other regulations. Provisions of the Virginia State Water Control Board regulations 9VAC25-91 and 9VAC25-580 addressing the maintenance and operational aspects of underground and above-ground storage tanks subject to those regulations are hereby incorporated by reference to be an enforceable part of this code. Where differences occur between the provisions of this code and the incorporated provisions of the State Water Control Board regulations, the provisions of the State Water Control Board regulations shall apply. Note: For requirements for the installation, repair, upgrade and closure of such tanks, see Section 414.6.2 of the USBC, Part I, Construction. | 5701.1.1 Other regulations. Provisions of the Virginia State Water Control Board regulations 9VAC25-91 and 9VAC25-580 addressing the maintenance and operational aspects of underground and aboveground storage tanks subject to those regulations are hereby incorporated by reference to be an enforceable part of this code. Where differences occur between the provisions of this code and the incorporated provisions of the State Water Control Board regulations, the provisions of the State Water Control Board regulations shall apply. Note: For requirements for the installation, repair, upgrade and closure of such tanks, see Section 414.6.2 of the USBC, Part I, Construction.
5701.2Nonapplicability. This chapter shall not apply to liquids as otherwise provided in other laws or regulations or chapters of this code, including: 1.Specific provisions for flammable liquids in motor fuel-dispensing facilities, repair garages, airports and marinas in Chapter 23. 2.Medicines, foodstuffs, cosmetics, and commercial, institutional and industrial products containing not more than 50 percent by volume of water-miscible liquids and with the remainder of the solution not being flammable, provided that such materials are packaged in individual containers not exceeding 1.3 gallons (5 L). 3.Quantities of alcoholic beverages in retail or wholesale sales or storage occupancies, providied that the liquids are packaged in individual containers not exceeding 1.3 gallons (5 L). 4.Storage and use of fuel oil in tanks and containers connected to oil-burning equipment. Such storage and use shall be in accordance with Section 603. For abandonment of fuel oil tanks, this chapter applies. 5.Refrigerant liquids and oils in refrigeration systems (see Section 606). 6.Storage and display of aerosol products complying with Chapter 51. 7.Storage and use of liquids that have no fire point when tested in accordance with ASTM D 92. 8.Liquids with a flash point greater than 95°F (35°C) in a water-miscible solution or dispersion with a water and inert (noncombustible) solids content of more than 80 percent by weight, which do not sustain combustion. 9.Liquids without flash points that can be flammable under some conditions, such as certain halogenated hydrocarbons and mixtures containing halogenated hydrocarbons. 10.The storage of distilled spirits and wines in wooden barrels and casks. | (N)5701.2 Applicability. This chapter shall apply to the maintenance and operation of flammable and combustible liquids.
5701.3Referenced documents. The applicable requirements of Chapter 50, other chapters of this code, the International Building Code and the International Mechanical Code pertaining to flammable liquids shall apply. | (N)5701.3 Referenced documents. (Section deleted)
5701.4Permits. Permits shall be required as set forth in Section 107.2. | 5701.4 Permits. Permits shall be required as set forth in Section 107.2.
5703.1Electrical. Electrical wiring and equipment shall be installed and maintained in accordance with Section 605 and NFPA 70. | N)5703.1 Electrical. Electrical wiring and equipment shall be maintained in accordance with the applicable building code.
5703.1.1Classified locations for flammable liquids. Areas where flammable liquids are stored, handled, dispensed or mixed shall be in accordance with Table 5703.1.1. A classified area shall not extend beyond an unpierced floor, roof or other solid partition. The extent of the classified area is allowed to be reduced, or eliminated, where sufficient technical justification is provided to the fire code official that a concentration in the area in excess of 25 percent of the lower flammable limit (LFL) cannot be generated. | (N)5703.1.1 Classified locations for flammable liquids. Areas where flammable liquids are stored, handled, dispensed or mixed shall be maintained in accordance with the applicable building code.
TABLE 5703.1.1 CLASS I ELECTRICAL EQUIPMENT LOCATIONSa | (N)TABLE 5703.1.1 CLASS I ELECTRICAL EQUIPMENT LOCATIONS (Table deleted)
5703.1.2Classified locations for combustible liquids. Areas where Class II or III liquids are heated above their flash points shall have electrical installations in accordance with Section 5703.1.1. Exception: Solvent distillation units in accordance with Section 5705.4. | (N)5702.1.2 Classified locations for combustible liquids. Areas where Class II or III liquids are heated above their flash points shall be maintained in accordance with the applicable building code.
5703.1.3Other applications. The fire code official is authorized to determine the extent of the Class I electrical equipment and wiring location when a condition is not specifically covered by these requirements or NFPA 70. | (N)5703.1.3 Other applications. (Section deleted)
5703.2Fire protection. Fire protection for the storage, use, dispensing, mixing, handling and on-site transportation of flammable and combustible liquids shall be in accordance with this chapter and applicable sections of Chapter 9. | (N)5703.2 Fire protection. Where provided, fire protection for the storage, use, dispensing, mixing, handling, and onsite transportation of flammable and combustible liquids shall be maintained in accordance with the applicable building code.
5703.6Piping systems. Piping systems, and their component parts, for flammable and combustible liquids shall be in accordance with Sections 5703.6.1 through 5703.6.11. | (N)5703.6 Piping systems. Piping systems, and their component parts, for flammable and combustible liquids shall be maintained in accordance with the applicable building code.
5703.6.1Nonapplicability. The provisions of Section 5703.6 shall not apply to gas or oil well installations; piping that is integral to stationary or portable engines, including aircraft, watercraft and motor vehicles; and piping in connection with boilers and pressure vessels regulated by the International Mechanical Code. | (N)5703.6.1 Nonapplicablility. (Section deleted) (N)5703.6.2 Design and fabrication of piping systems and components. (Section deleted)
TABLE 5703.6.2 PIPING STANDARDS | (N)TABLE 5703.6.2 PIPING STANDARDS (Table deleted)
5703.6.2.1Special materials. Low-melting-point materials (such as aluminum, copper or brass), materials that soften on fire exposure (such as nonmetallic materials) and nonductile material (such as cast iron) shall be acceptable for use underground in accordance with the applicable standard listed in Table 5703.6.2. When such materials are used outdoors in above-ground piping systems or within buildings, they shall be in accordance with the applicable standard listed in Table 5703.6.2 and one of the following: 1.Suitably protected against fire exposure. 2.Located where leakage from failure would not unduly expose people or structures. 3.Located where leakage can be readily controlled by operation of accessible remotely located valves. In all cases, nonmetallic piping shall be used in accordance with Section 27.4.6 of NFPA 30. 5703.6.3Testing. Unless tested in accordance with the applicable section of ASME B31.9, piping, before being covered, enclosed or placed in use, shall be hydrostatically tested to 150 percent of the maximum anticipated pressure of the system, or pneumatically tested to 110 percent of the maximum anticipated pressure of the system, but not less than 5 pounds per square inch gauge (psig) (34.47 kPa) at the highest point of the system. This test shall be maintained for a sufficient time period to complete visual inspection of joints and connections. For a minimum of 10 minutes, there shall be no leakage or permanent distortion. Care shall be exercised to ensure that these pressures are not applied to vented storage tanks. Such storage tanks shall be tested independently from the piping. | (N)5703.6.2.1 Special materials. (Section deleted) (N)5703.6.3 Testing. (Section deleted)
5703.6.3.1Existing piping. Existing piping shall be tested in accordance with this section when the fire code official has reasonable cause to believe that a leak exists. Piping that could contain flammable or combustible liquids shall not be tested pneumatically. Such tests shall be at the expense of the owner or operator. Exception: Vapor-recovery piping is allowed to be tested using an inert gas. | (N)5703.6.3.1 Existing piping. Existing piping shall be tested in accordance with the applicable building code where the fire official has reasonable cause to believe that a leak exists.
5703.6.4Protection from vehicles. Guard posts or other approved means shall be provided to protect piping, valves or fittings subject to vehicular damage in accordance with Section 312. 5703.6.5Protection from external corrosion and galvanic action. Where subject to external corrosion, piping, related fluid-handling components and supports for both underground and above-ground applications shall be fabricated from noncorrosive materials, and coated or provided with corrosion protection. Dissimilar metallic parts that promote galvanic action shall not be joined. 5703.6.6Valves. Piping systems shall contain a sufficient number of manual control valves and check valves to operate the system properly and to protect the plant under both normal and emergency conditions. Piping systems in connection with pumps shall contain a sufficient number of such valves to control properly the flow of liquids in normal operation and in the event of physical damage or fire exposure. 5703.6.6.1Backflow protections. Connections to pipelines or piping by which equipment (such as tank cars, tank vehicles or marine vessels) discharges liquids into storage tanks shall be provided with check valves or block valves for automatic protection against backflow where the piping arrangement is such that backflow from the system is possible. Where loading and unloading is done through a common pipe system, a check valve is not required. However, a block valve shall be provided which is located so as to be readily accessible or remotely operable. 5703.6.6.2Manual drainage. Manual drainage-control valves shall be located at approved locations remote from the tanks, diked area, drainage system and impounding basin to ensure their operation in a fire condition. 5703.6.7Connections. Above-ground tanks with connections located below normal liquid level shall be provided with internal or external isolation valves located as close as practical to the shell of the tank. Except for liquids whose chemical characteristics are incompatible with steel, such valves, when external, and their connections to the tank shall be of steel. 5703.6.8Piping supports. Piping systems shall be substantially supported and protected against physical damage and excessive stresses arising from settlement, vibration, expansion, contraction or exposure to fire. The supports shall be protected against exposure to fire by one of the following: 1.Draining liquid away from the piping system at a minimum slope of not less than 1 percent. 2.Providing protection with a fire-resistance rating of not less than 2 hours. 3.Other approved methods. 5703.6.9Flexible joints. Flexible joints shall be listed and approved and shall be installed on underground liquid, vapor and vent piping at all of the following locations: 1.Where piping connects to underground tanks. 2.Where piping ends at pump islands and vent risers. 3.At points where differential movement in the piping can occur. 5703.6.9.1Fiberglass-reinforced plastic piping. Fiberglass-reinforced plastic (FRP) piping is not required to be provided with flexible joints in locations where both of the following conditions are present: 1.Piping does not exceed 4 inches (102 mm) in diameter. 2.Piping has a straight run of not less than 4 feet (1219 mm) on one side of the connection when such connections result in a change of direction. In lieu of the minimum 4-foot (1219 mm) straight run length, approved and listed flexible joints are allowed to be used under dispensers and suction pumps, at submerged pumps and tanks, and where vents extend above ground. 5703.6.10Pipe joints. Joints shall be liquid tight and shall be welded, flanged or threaded except that listed flexible connectors are allowed in accordance with Section 5703.6.9. Threaded or flanged joints shall fit tightly by using approved methods and materials for the type of joint. Joints in piping systems used for Class I liquids shall be welded when located in concealed spaces within buildings. Nonmetallic joints shall be approved and shall be installed in accordance with the manufacturer’s instructions. Pipe joints that are dependent on the friction characteristics or resiliency of combustible materials for liquid tightness of piping shall not be used in buildings. Piping shall be secured to prevent disengagement at the fitting. 5703.6.11Bends. Pipe and tubing shall be bent in accordance with ASME B31.9. | (N)5703.6.4 Protection from vehicles. (Section deleted) (N)5703.6.5 Protection from external corrosion and galvanic action. (Section deleted) (N)5703.6.6 Valves. (Section deleted) (N)5703.6.6.1 Backflow protections. (Section deleted) (N)5703.6.6.2 Manual drainage. (Section deleted) (N)5703.6.7 Connections. (Section deleted) (N)5703.6.8 Piping supports. (Section deleted) (N)5703.6.9 Flexible joints. (Section deleted) (N)5703.6.9.1 Fiberglass-reinforced plastic piping. (Section deleted) (N)5703.6.10 Pipe joints. (Section deleted) (N)5703.6.11 Bends. (Section deleted)
5704.2.5Explosion control. Explosion control shall be provided in accordance with Section 911. | Delete Section 5704.2.5. (N)5704.2.5 Explosion control. (Section deleted)
5704.2.7Design, construction and general installation requirements for tanks. The design, fabrication and construction of tanks shall comply with NFPA 30. Each tank shall bear a permanent nameplate or marking indicating the standard used as the basis of design. 5704.2.7.1Materials used in tank construction. The materials used in tank construction shall be in accordance with NFPA 30. 5704.2.7.2Pressure limitations for tanks. Tanks shall be designed for the pressures to which they will be subjected in accordance with NFPA 30. 5704.2.7.3Tank vents for normal venting. Tank vents for normal venting shall be installed and maintained in accordance with Sections 5704.2.7.3.1 through 5704.2.7.3.6. 5704.2.7.3.1Vent lines. Vent lines from tanks shall not be used for purposes other than venting unless approved. 5704.2.7.3.2Vent-line flame arresters and pressure-vacuum vents. Listed or approved flame arresters or pressure-vacuum (PV) vents that remain closed unless venting under pressure or vacuum conditions shall be installed in normal vents of tanks containing Class IB and IC liquids. Exception: When determined by the fire code official that the use of such devices can result in damage to the tank. Vent-line flame arresters shall be installed in accordance with their listing or API 2000 and maintained in accordance with Section 21.8.6 of NFPA 30 or API 2000. In-line flame arresters in piping systems shall be installed and maintained in accordance with their listing or API 2028. Pressure-vacuum vents shall be installed in accordance with Section 21.4.3 of NFPA 30 or API 2000 and maintained in accordance with Section 21.8.6 of NFPA 30 or API 2000. 5704.2.7.3.3Vent pipe outlets. Vent pipe outlets for tanks storing Class I, II or IIIA liquids shall be located such that the vapors are released at a safe point outside of buildings and not less than 12 feet (3658 mm) above the finished ground level. Vapors shall be discharged upward or horizontally away from adjacent walls to assist in vapor dispersion. Vent outlets shall be located such that flammable vapors will not be trapped by eaves or other obstructions and shall be at least 5 feet (1524 mm) from building openings or lot lines of properties that can be built upon. Vent outlets on atmospheric tanks storing Class IIIB liquids are allowed to discharge inside a building if the vent is a normally closed vent. Exception: Vent pipe outlets on tanks storing Class IIIB liquid inside buildings and connected to fuel-burning equipment shall be located such that the vapors are released to a safe location outside of buildings. 5704.2.7.3.4Installation of vent piping. Vent piping shall be designed, sized, constructed and installed in accordance with Section 5703.6. Vent pipes shall be installed such that they will drain toward the tank without sags or traps in which liquid can collect. Vent pipes shall be installed in such a manner so as not to be subject to physical damage or vibration. 5704.2.7.3.5Manifolding. Tank vent piping shall not be manifolded unless required for special purposes such as vapor recovery, vapor conservation or air pollution control. 5704.2.7.3.5.1Above-ground tanks. For above-ground tanks, manifolded vent pipes shall be adequately sized to prevent system pressure limits from being exceeded when manifolded tanks are subject to the same fire exposure. 5704.2.7.3.5.2Underground tanks. For underground tanks, manifolded vent pipes shall be sized to prevent system pressure limits from being exceeded when manifolded tanks are filled simultaneously. 5704.2.7.3.5.3Tanks storing Class I liquids. Vent piping for tanks storing Class I liquids shall not be manifolded with vent piping for tanks storing Class II and III liquids unless positive means are provided to prevent the vapors from Class I liquids from entering tanks storing Class II and III liquids, to prevent contamination and possible change in classification of less volatile liquid. | Delete Sections 5704.2.7 through 5704.2.7.3.5.3. (N)5704.2.7 Design, fabrication and construction requirements for tanks. (Section deleted) (N)5704.2.7.1 Materials used in tank construction. (Section deleted) (N)5704.2.7.2 Pressure limitations for tanks. (Section deleted) (N)5704.2.7.3 Tank vents for normal venting. (Section deleted) (N)5704.2.7.3.1 Vent lines. (Section deleted) (N)5704.2.7.3.2 Vent-line flame arresters and pressure-vacuum vents. (Section deleted) (N)5704.2.7.3.3 Vent pipe outlets. (Section deleted) (N)5704.2.7.3.4 Installation of vent piping. (Section deleted) (N)5704.2.7.3.5 Manifolding. (Section deleted) (N)5704.2.7.3.5.1 Above-ground tanks. (Section deleted) (N)5704.2.7.3.5.2 Underground tanks. (Section deleted) (N)5704.2.7.3.5.3 Tanks storing Class I liquids. (Section deleted)
5704.2.7.4Emergency venting. Stationary, above-ground tanks shall be equipped with additional venting that will relieve excessive internal pressure caused by exposure to fires. Emergency vents for Class I, II and IIIA liquids shall not discharge inside buildings. The venting shall be installed and maintained in accordance with Section 22.7 of NFPA 30. Exceptions: 1.Tanks larger than 12,000 gallons (45 420 L) in capacity storing Class IIIB liquids which are not within the diked area or the drainage path of Class I or II liquids do not require emergency relief venting. 2.Emergency vents on protected above-ground tanks complying with UL 2085 containing Class II or IIIA liquids are allowed to discharge inside the building. | (N)5704.2.7.4 Emergency venting. Where required, emergency venting for stationary, aboveground tanks shall be maintained in accordance with the applicable building code.
5704.2.7.5Tank openings other than vents. Tank openings for other than vents shall comply with Sections 5704.2.7.5.1 through 5704.2.7.5.8. 5704.2.7.5.1Connections below liquid level. Connections for tank openings below the liquid level shall be liquid tight. | (N)5704.2.7.5 Tank openings other than vents. (Section deleted) (N)5704.2.7.5.1 Connections below liquid level. (Section deleted)
5704.2.7.5.3Piping, connections and fittings. Piping, connections, fittings and other appurtenances shall be installed in accordance with Section 5703.6. | (N)5704.2.7.5.3 Piping, connections and fittings. (Section deleted)
5704.2.7.5.5Fill pipes and discharge lines. For top-loaded tanks, a metallic fill pipe shall be designed and installed to minimize the generation of static electricity by terminating the pipe within 6 inches (152 mm) of the bottom of the tank, and it shall be installed in a manner which avoids excessive vibration. 5704.2.7.5.5.1Class I liquids. For Class I liquids other than crude oil, gasoline and asphalt, the fill pipe shall be designed and installed in a manner which will minimize the possibility of generating static electricity by terminating within 6 inches (152 mm) of the bottom of the tank. 5704.2.7.5.5.2Underground tanks. For underground tanks, fill pipe and discharge lines shall enter only through the top. Fill lines shall be sloped toward the tank. Underground tanks for Class I liquids having a capacity greater than 1,000 gallons (3785 L) shall be equipped with a tight fill device for connecting the fill hose to the tank. | (N)5704.2.7.5.5 Fill pipes and discharge lines. (Section deleted) (N)5704.2.7.5.5.1 Class I liquids. (Section deleted) (N)5704.2.7.5.5.2 Underground tanks. (Section deleted)
5704.2.7.5.7Protection against vapor release. Tank openings provided for purposes of vapor recovery shall be protected against possible vapor release by means of a spring-loaded check valve or dry-break connections, or other approved device, unless the opening is a pipe connected to a vapor processing system. Openings designed for combined fill and vapor recovery shall also be protected against vapor release unless connection of the liquid delivery line to the fill pipe simultaneously connects the vapor recovery line. Connections shall be vapor tight. | (N)5704.2.7.5.7 Protection against vapor release. (Section deleted) (N)5704.2.7.5.8 Overfill prevention. (Section deleted)
5704.2.7.6Repair, alteration or reconstruction of tanks and piping. The repair, alteration or reconstruction, including welding, cutting and hot tapping of storage tanks and piping that have been placed in service, shall be in accordance with NFPA 30. | (N)5704.2.7.6 Repair, alteration or reconstruction of tanks and piping. Hot work, as defined in Section 202, on storage tanks shall be conducted in accordance with Section 3510.
5704.2.7.7Design of supports. The design of the supporting structure for tanks shall be in accordance with the International Building Code and NFPA 30. | (N)5704.2.7.7 Design of supports. (Section deleted) (N)5704.2.7.8 Locations subject to flooding. (Section deleted) (N)5704.2.7.9 Corrosion protection. (Section deleted)
5704.2.7.11Tank lining. Steel tanks are allowed to be lined only for the purpose of protecting the interior from corrosion or providing compatibility with a material to be stored. Only those liquids tested for compatibility with the lining material are allowed to be stored in lined tanks. | (N)5704.2.7.11 Tank lining. (Section deleted) (N)5704.2.8 Vaults. (Section deleted) (N)5704.2.8.1 Listing required. (Section deleted) (N)5704.2.8.2 Design and construction. (Section deleted) (N)5704.2.8.3 Secondary containment. (Section deleted)
5704.2.8.5Anchoring. Vaults and their tanks shall be suitably anchored to withstand uplifting by ground water or flooding, including when the tank is empty. | (N)5704.2.8.5 Anchoring. Anchoring for vaults shall be maintained in accordance with the applicable building code.
5704.2.8.7Arrangement. Tanks shall be listed for above-ground use, and each tank shall be in its own vault. Compartmentalized tanks shall be allowed and shall be considered as a single tank. Adjacent vaults shall be allowed to share a common wall. The common wall shall be liquid and vapor tight and shall be designed to withstand the load imposed when the vault on either side of the wall is filled with water. 5704.2.8.8Connections. Connections shall be provided to permit venting of each vault to dilute, disperse and remove vapors prior to personnel entering the vault. | (N)5704.2.8.7 Arrangement. (Section deleted) (N)5704.2.8.8 Connections. (Section deleted)
5704.2.8.9Ventilation. Vaults that contain tanks of Class I liquids shall be provided with an exhaust ventilation system installed in accordance with Section 5004.3. The ventilation system shall operate continuously or be designed to operate upon activation of the vapor or liquid detection system. The system shall provide ventilation at a rate of not less than 1 cubic foot per minute (cfm) per square foot of floor area [0.00508 m3/(s • m2)], but not less than 150 cfm (4 m3/min). The exhaust system shall be designed to provide air movement across all parts of the vault floor. Supply and exhaust ducts shall extend to within 3 inches (76 mm), but not more than 12 inches (305 mm), of the floor. The exhaust system shall be installed in accordance with the International Mechanical Code. | (N)5704.2.8.9 Ventilation. Where required, the exhaust system shall be maintained in accordance with the applicable building code
5704.2.8.10Liquid detection. Vaults shall be equipped with a detection system capable of detecting liquids, including water, and activating an alarm. 5704.2.8.11Monitoring and detection. Vaults shall be provided with approved vapor and liquid detection systems and equipped with on-site audible and visual warning devices with battery backup. Vapor detection systems shall sound an alarm when the system detects vapors that reach or exceed 25 percent of the lower explosive limit (LEL) of the liquid stored. Vapor detectors shall be located no higher than 12 inches (305 mm) above the lowest point in the vault. Liquid detection systems shall sound an alarm upon detection of any liquid, including water. Liquid detectors shall be located in accordance with the manufacturer’s instructions. Activation of either vapor or liquid detection systems shall cause a signal to be sounded at an approved, constantly attended location within the facility serving the tanks or at an approved location. Activation of vapor detection systems shall also shut off dispenser pumps. | (N)5704.2.8.10 Liquid detection. (Section deleted) (N)5704.2.8.11 Monitoring and detection. (Section deleted)
5704.2.8.13Normal vents. Vent pipes that are provided for normal tank venting shall terminate at least 12 feet (3658 mm) above ground level. 5704.2.8.14Emergency vents. Emergency vents shall be vapor tight and shall be allowed to discharge inside the vault. Long-bolt manhole covers shall not be allowed for this purpose. | (N)5704.2.8.13 Normal vents. (Section deleted) (N)5704.2.8.14 Emergency vents. (Section deleted)
5704.2.8.16Fire protection. Vaults shall be provided with a suitable means to admit a fire suppression agent. | (N)5704.2.8.16 Fire protection. (Section deleted)
5704.2.8.18Overfill protection. Overfill protection shall be provided in accordance with Section 5704.2.9.7.6. The use of a float vent valve shall be prohibited. | (N)5704.2.8.18 Overfill protection. (Section deleted)
5704.2.9Above-ground tanks. Above-ground storage of flammable and combustible liquids in tanks shall comply with Section 5704.2 and Sections 5704.2.9.1 through 5704.2.9.7.10. 5704.2.9.1Existing noncompliant installations. Existing above-ground tanks shall be maintained in accordance with the code requirements that were applicable at the time of installation. Above-ground tanks that were installed in violation of code requirements applicable at the time of installation shall be made code compliant or shall be removed in accordance with Section 5704.2.14, regardless of whether such tank has been previously inspected (see Section 106.4). | (N)5704.2.9 Aboveground tanks. Aboveground storage of flammable and combustible liquids in tanks shall be maintained in accordance with the applicable building code. (N)5704.2.9.1 Existing noncompliant installations. Existing aboveground tanks shall be maintained in accordance with the code requirements that were applicable at the time of installation.
5704.2.9.2Fire protection. Fire protection for above-ground tanks shall comply with Sections 5704.2.9.2.1 through 5704.2.9.2.4. 5704.2.9.2.1Required foam fire protection systems. When required by the fire code official, foam fire protection shall be provided for above-ground tanks, other than pressure tanks operating at or above 1 pound per square inch gauge (psig) (6.89 kPa) when such tank, or group of tanks spaced less than 50 feet (15 240 mm) apart measured shell to shell, has a liquid surface area in excess of 1,500 square feet (139 m2), and is in accordance with one of the following: 1.Used for the storage of Class I or II liquids. 2.Used for the storage of crude oil. 3.Used for in-process products and is located within 100 feet (30 480 mm) of a fired still, heater, related fractioning or processing apparatus or similar device at a processing plant or petroleum refinery as herein defined. 4.Considered by the fire code official as posing an unusual exposure hazard because of topographical conditions; nature of occupancy, proximity on the same or adjoining property, and height and character of liquids to be stored; degree of private fire protection to be provided; and facilities of the fire department to cope with flammable liquid fires. 5704.2.9.2.2Foam fire protection system installation. Where foam fire protection is required, it shall be installed in accordance with NFPA 11. 5704.2.9.2.2.1Foam storage. Where foam fire protection is required, foam-producing materials shall be stored on the premises. Exception: Storage of foam-producing materials off the premises is allowed as follows: 1.Such materials stored off the premises shall be of the proper type suitable for use with the equipment at the installation where required. 2.Such materials shall be readily available at the storage location at all times. 3.Adequate loading and transportation facilities shall be provided. 4.The time required to deliver such materials to the required location in the event of fire shall be consistent with the hazards and fire scenarios for which the foam supply is intended. 5.At the time of a fire, these off-premises supplies shall be accumulated in sufficient quantities before placing the equipment in operation to ensure foam production at an adequate rate without interruption until extinguishment is accomplished. 5704.2.9.2.3Fire protection of supports. Supports or pilings for above-ground tanks storing Class I, II or IIIA liquids elevated more than 12 inches (305 mm) above grade shall have a fire-resistance rating of not less than 2 hours in accordance with the fire exposure criteria specified in ASTM E 1529. Exceptions: 1.Structural supports tested as part of a protected above-ground tank in accordance with UL 2085. 2.Stationary tanks located outside of buildings when protected by an approved water-spray system designed in accordance with Chapter 9 and NFPA 15. 3.Stationary tanks located inside of buildings equipped throughout with an approved automatic sprinkler system designed in accordance with Section 903.3.1.1. | (N)5704.2.9.2 Fire protection. (Section deleted) (N)5704.2.9.2.1 Required foam fire protection systems. (Section deleted) (N)5704.2.9.2.2 Foam fire protection system installation. (Section deleted) (N)5704.2.9.2.2.1 Foam storage. (Section deleted) (N)5704.2.9.2.3 Fire protection of supports. (Section deleted)
5704.2.9.3Supports, foundations and anchorage. Supports, foundations and anchorages for above-ground tanks shall be designed and constructed in accordance with NFPA 30 and the International Building Code. | (N)5704.2.9.3 Supports, foundations and anchorage. (Section deleted)
5704.2.9.4Stairs, platforms and walkways. Stairs, platforms and walkways shall be of noncombustible construction and shall be designed and constructed in accordance with NFPA 30 and the International Building Code. | (N)5704.2.9.4 Stairways, platforms and walkways. Stairways, platforms and walkways shall be maintained in accordance with the applicable building code. (N)5704.2.9.5 Aboveground tanks inside of buildings. Aboveground tanks inside of buildings shall be maintained in accordance with the applicable building code.
5704.2.9.5.1Overfill prevention. Above-ground tanks storing Class I, II and IIIA liquids inside buildings shall be equipped with a device or other means to prevent overflow into the building including, but not limited to: a float valve; a preset meter on the fill line; a valve actuated by the weight of the tank’s contents; a low-head pump that is incapable of producing overflow; or a liquid-tight overflow pipe at least one pipe size larger than the fill pipe and discharging by gravity back to the outside source of liquid or to an approved location. Tanks containing Class IIIB liquids and connected to fuel-burning equipment shall be provided with a means to prevent overflow into buildings in accordance with Section 5704.2.7.5.8. 5704.2.9.5.2Fill pipe connections. Fill pipe connections for tanks storing Class I, II and IIIA liquids and Class IIIB liquids connected to fuel-burning equipment shall be in accordance with Section 5704.2.9.7.7. | (N)5704.2.9.5.1 Overfill prevention. (Section deleted) (N)5704.2.9.5.2 Fill pipe connections. (Section deleted)
5704.2.9.6Above-ground tanks outside of buildings. Above-ground tanks outside of buildings shall comply with Sections 5704.2.9.6.1 through 5704.2.9.6.3. | (N)5704.2.9.6 Aboveground tanks outside of buildings. Aboveground tanks outside of buildings shall be maintained in accordance with the applicable building code.
5704.2.9.6.1Locations where above-ground tanks are prohibited. Storage of Class I and II liquids in above-ground tanks outside of buildings is prohibited within the limits established by law as the limits of districts in which such storage is prohibited (see Section 3 of the Sample Legislation for Adoption of the International Fire Code on page xxi). 5704.2.9.6.1.1Location of tanks with pressures 2.5 psig or less. Above-ground tanks operating at pressures not exceeding 2.5 psig (17.2 kPa) for storage of Class I, II or IIIA liquids, which are designed with a floating roof, a weak roof-to-shell seam or equipped with emergency venting devices limiting pressure to 2.5 psig (17.2 kPa), shall be located in accordance with Table 22.4.1.1(a) of NFPA 30. Exceptions: 1.Vertical tanks having a weak roof-to-shell seam and storing Class IIIA liquids are allowed to be located at one-half the distances specified in Table 22.4.1.1(a) of NFPA 30, provided the tanks are not within a diked area or drainage path for a tank storing Class I or II liquids. 2.Liquids with boilover characteristics and unstable liquids in accordance with Sections 5704.2.9.6.1.3 and 5704.2.9.6.1.4. 3.For protected above-ground tanks in accordance with Section 5704.2.9.7 and tanks in at-grade or above-grade vaults in accordance with Section 5704.2.8, the distances in Table 22.4.1.1(b) of NFPA 30 shall apply and shall be reduced by one-half, but not to less than 5 feet (1524 mm). 5704.2.9.6.1.2Location of tanks with pressures exceeding 2.5 psig. Above-ground tanks for the storage of Class I, II or IIIA liquids operating at pressures exceeding 2.5 psig (17.2 kPa) or equipped with emergency venting allowing pressures to exceed 2.5 psig (17.2 kPa) shall be located in accordance with Table 22.4.1.3 of NFPA 30. Exception: Liquids with boilover characteristics and unstable liquids in accordance with Sections 5704.2.9.6.1.4 and 5704.2.9.6.1.5. 5704.2.9.6.1.3Location of tanks storing boilover liquids. Above-ground tanks for storage of liquids with boilover characteristics shall be located in accordance with Table 22.4.1.4 of NFPA 30. 5704.2.9.6.1.4Location of tanks storing unstable liquids. Above-ground tanks for the storage of unstable liquids shall be located in accordance with Table 22.4.1.5 of NFPA 30. 5704.2.9.6.1.5Location of tanks storing Class IIIB liquids. Above-ground tanks for the storage of Class IIIB liquids, excluding unstable liquids, shall be located in accordance with Table 22.4.1.6 of NFPA 30, except when located within a diked area or drainage path for a tank or tanks storing Class I or II liquids. Where a Class IIIB liquid storage tank is within the diked area or drainage path for a Class I or II liquid, distances required by Section 5704.2.9.6.1.1 shall apply. 5704.2.9.6.1.6Reduction of separation distances to adjacent property. Where two tank properties of diverse ownership have a common boundary, the fire code official is authorized to, with the written consent of the owners of the two properties, apply the distances in Sections 5704.2.9.6.1.2 through 5704.2.9.6.1.5 assuming a single property. 5704.2.9.6.2Separation between adjacent stable or unstable liquid tanks. The separation between tanks containing stable liquids shall be in accordance with Table 22.4.2.1 of NFPA 30. Where tanks are in a diked area containing Class I or II liquids, or in the drainage path of Class I or II liquids, and are compacted in three or more rows or in an irregular pattern, the fire code official is authorized to require greater separation than specified in Table 22.4.2.1 of NFPA 30 or other means to make tanks in the interior of the pattern accessible for fire-fighting purposes. Exception: Tanks used for storing Class IIIB liquids are allowed to be spaced 3 feet (914 mm) apart unless within a diked area or drainage path for a tank storing Class I or II liquids. The separation between tanks containing unstable liquids shall not be less than one-half the sum of their diameters. 5704.2.9.6.3Separation between adjacent tanks containing flammable or combustible liquids and LP-gas. The minimum horizontal separation between an LP-gas container and a Class I, II or IIIA liquid storage tank shall be 20 feet (6096 mm) except in the case of Class I, II or IIIA liquid tanks operating at pressures exceeding 2.5 psig (17.2 kPa) or equipped with emergency venting allowing pressures to exceed 2.5 psig (17.2 kPa), in which case the provisions of Section 5704.2.9.6.2 shall apply. An approved means shall be provided to prevent the accumulation of Class I, II or IIIA liquids under adjacent LP-gas containers such as by dikes, diversion curbs or grading. When flammable or combustible liquid storage tanks are within a diked area, the LP-gas containers shall be outside the diked area and at least 10 feet (3048 mm) away from the centerline of the wall of the diked area. Exceptions: 1.Liquefied petroleum gas containers of 125 gallons (473 L) or less in capacity installed adjacent to fuel-oil supply tanks of 660 gallons (2498 L) or less in capacity. 2.Horizontal separation is not required between above-ground LP-gas containers and underground flammable and combustible liquid tanks. | (N)5704.2.9.6.1 Locations where aboveground tanks are prohibited. (Section deleted) (N)5704.2.9.6.1.1 Location of tanks with pressures 2.5 psig or less. (Section deleted) (N)5704.2.9.6.1.2 Location of tanks with pressures exceeding 2.5 psig. (Section deleted) (N)5704.2.9.6.1.3 Location of tanks storing boilover liquids. (Section deleted) (N)5704.2.9.6.1.4 Location of tanks storing unstable liquids. (Section deleted) (N)5704.2.9.6.1.5 Location of tanks storing Class IIIB liquids. (Section deleted) (N)5704.2.9.6.1.6 Reduction of separation distances to adjacent property. (Section deleted) (N)5704.2.9.6.2 Separation between adjacent stable or unstable liquid tanks. (Section deleted) (N)5704.2.9.6.3 Separation between adjacent tanks containing flammable or combustible liquids and LP-gas. (Section deleted)
5704.2.9.7Additional requirements for protected above-ground tanks. In addition to the requirements of this chapter for above-ground tanks, the installation of protected above-ground tanks shall be in accordance with Sections 5704.2.9.7.1 through 5704.2.9.7.10. 5704.2.9.7.1Tank construction. The construction of a protected above-ground tank and its primary tank shall be in accordance with Section 5704.2.7. 5704.2.9.7.2Normal and emergency venting. Normal and emergency venting for protected above-ground tanks shall be provided in accordance with Sections 5704.2.7.3 and 5704.2.7.4. The vent capacity reduction factor shall not be allowed. 5704.2.9.7.3Flame arresters. Approved flame arresters or pressure vacuum breather valves shall be installed in normal vents. 5704.2.9.7.4Secondary containment. Protected above-ground tanks shall be provided with secondary containment, drainage control or diking in accordance with Section 5004.2. A means shall be provided to establish the integrity of the secondary containment in accordance with NFPA 30. | (N)5704.1.9.7 Additional requirements for protected above-ground tanks. (Section deleted) (N)5704.1.9.7.1 Tanks construction. (Section deleted) (N)5704.1.9.7.2 Normal and emergency venting. (Section deleted) (N)5704.1.9.7.3 Secondary containment. (Section deleted)
5704.2.9.7.6Overfill prevention. Protected above-ground tanks shall not be filled in excess of 95 percent of their capacity. An overfill prevention system shall be provided for each tank. During tank-filling operations, the system shall comply with one of the following: 1.The system shall: 1.1.Provide an independent means of notifying the person filling the tank that the fluid level has reached 90 percent of tank capacity by providing an audible or visual alarm signal, providing a tank level gauge marked at 90 percent of tank capacity, or other approved means; and 1.2.Automatically shut off the flow of fuel to the tank when the quantity of liquid in the tank reaches 95 percent of tank capacity. For rigid hose fuel-delivery systems, an approved means shall be provided to empty the fill hose into the tank after the automatic shutoff device is activated. 2.The system shall reduce the flow rate to not more than 15 gallons per minute (0.95 L/s) so that at the reduced flow rate, the tank will not overfill for 30 minutes, and automatically shut off flow into the tank so that none of the fittings on the top of the tank are exposed to product because of overfilling. | (N)5704.2.9.7.5 Overfill prevention. (Section deleted)
5704.2.9.7.6.2Determination of available tank capacity. The filling procedure shall require the person filling the tank to determine the gallonage (literage) required to fill it to 90 percent of capacity before commencing the fill operation. | (N)5704.2.9.7.5.2 Determination of availability. (Section deleted)
5704.2.9.7.7Fill pipe connections. The fill pipe shall be provided with a means for making a direct connection to the tank vehicle’s fuel delivery hose so that the delivery of fuel is not exposed to the open air during the filling operation. Where any portion of the fill pipe exterior to the tank extends below the level of the top of the tank, a check valve shall be installed in the fill pipe not more than 12 inches (305 mm) from the fill hose connection. | (N)5704.2.9.7.6 Fill pipe connections. (Section deleted)
5704.2.9.7.9Tank openings. Tank openings in protected above-ground tanks shall be through the top only. | (N)5704.2.9.7.8 Tank openings. (Section deleted) (N)5704.2.9.7.9 Antisiphon devices. (Section deleted) (N)5704.2.10 Drainage and diking. (Section deleted) (N)5704.2.10.1 Volumetric capacity. (Section deleted) (N)5704.2.10.2 Diked areas containing two or more tanks. (Section deleted) (N)5704.2.10.3 Protection of piping from exposure fires. (Section deleted)
5704.2.10.5Equipment, controls and piping in diked areas. Pumps, manifolds and fire protection equipment or controls shall not be located within diked areas or drainage basins or in a location where such equipment and controls would be endangered by fire in the diked area or drainage basin. Piping above ground shall be minimized and located as close as practical to the shell of the tank in diked areas or drainage basins. Exceptions: 1.Pumps, manifolds and piping integral to the tanks or equipment being served which is protected by intermediate diking, berms, drainage or fire protection such as water spray, monitors or resistive coating. 2.Fire protection equipment or controls which are appurtenances to the tanks or equipment being protected, such as foam chambers or foam piping and water or foam monitors and hydrants, or hand and wheeled extinguishers. | (N)5704.2.10.5 Equipment, controls and piping in diked areas. (Section deleted)
5704.2.11Underground tanks. Underground storage of flammable and combustible liquids in tanks shall comply with Section 5704.2 and Sections 5704.2.11.1 through 5704.2.11.5.2. | (N)5704.2.11 Underground tanks. Underground storage of flammable and combustible liquids in tanks shall be maintained in accordance with the applicable building code.
5704.2.11.2Location. Flammable and combustible liquid storage tanks located underground, either outside or under buildings, shall be in accordance with all of the following: 1.Tanks shall be located with respect to existing foundations and supports such that the loads carried by the latter cannot be transmitted to the tank. 2.The distance from any part of a tank storing liquids to the nearest wall of a basement, pit, cellar or lot line shall not be less than 3 feet (914 mm). 3.A minimum distance of 1 foot (305 mm), shell to shell, shall be maintained between underground tanks. | (N)5704.2.11.1 Location. The location of flammable and combustible liquid storage tanks located underground, either outside or under buildings, shall be in accordance with the applicable building code.
5704.2.11.3Depth and cover. Excavation for underground storage tanks shall be made with due care to avoid undermining of foundations of existing structures. Underground tanks shall be set on firm foundations and surrounded with at least 6 inches (152 mm) of noncorrosive inert material, such as clean sand. 5704.2.11.4Overfill protection and prevention systems. Fill pipes shall be equipped with a spill container and an overfill prevention system in accordance with NFPA 30. | (N)5704.2.11.2 Depth and cover. (Section deleted) (N)5704.2.11.3 Overfill protection and prevention systems. (Section deleted)
5704.2.11.5Leak prevention. Leak prevention for underground tanks shall comply with Sections 5704.2.11.5.1 and 5704.2.11.5.2. | (N)5704.2.11.4 Leak prevention. (Section deleted)
5704.2.11.5.2Leak detection. Underground storage tank systems shall be provided with an approved method of leak detection from any component of the system that is designed and installed in accordance with NFPA 30. | (N)5704.2.11.4.2 Leak detection. (Section deleted)
Exception: Underground storage tanks subject to the Virginia State Water Control Board regulation 9VAC25-580. | Add the following exception to Section 5704.2.13.1.3 to read: Exception: Underground storage tanks subject to the Virginia State Water Control Board regulation 9VAC25-580.
5704.2.12.2Testing of underground tanks. Before being covered or placed in use, tanks and piping connected to underground tanks shall be tested for tightness in the presence of the fire code official. Piping shall be tested in accordance with Section 5703.6.3. The system shall not be covered until it has been approved. | 5704.2.12.2 Testing of underground tanks. Before being covered or placed in use, tanks and piping connected to underground tanks shall be tested for tightness in the presence of the fire code official. Piping shall be tested in accordance with the applicable building code. The system shall not be covered until it has been approved.
5704.2.13.1.2Out of service for 90 days. Underground tanks not used for a period of 90 days shall be safeguarded in accordance with all the following or be removed in accordance with Section 5704.2.14: 1.Flammable or combustible liquids shall be removed from the tank. 2.All piping, including fill line, gauge opening, vapor return and pump connection, shall be capped or plugged and secured from tampering. 3.Vent lines shall remain open and be maintained in accordance with Sections 5704.2.7.3 and 5704.2.7.4. | 5704.2.13.1.2 Out of service for 90 days. Underground tanks not used for a period of 90 days shall be safeguarded in accordance with all the following or be removed in accordance with Section 5704.2.14: 1. Flammable or combustible liquids shall be removed from the tank. 2. All piping, including fill line, gauge opening, vapor return and pump connection, shall be capped or plugged and secured from tampering. FLAMMABLE AND COMBUSTIBLE LIQUIDS 204 2015 VIRGINIA STATEWIDE FIRE PREVENTION CODE 3. Vent lines shall remain open and be maintained in accordance with Section 5704.2.7.4.
5704.2.13.1.5Reinstallation of underground tanks. Tanks which are to be reinstalled for flammable or combustible liquid service shall be in accordance with this chapter, ASME Boiler and Pressure Vessel Code (Section VIII), API 12-P, API 1615, UL 58 and UL 1316. | (N)5704.2.13.1.5 Reinstallation of underground tanks. Tanks that are to be reinstalled for flammable or combustible liquid service shall be approved by the building official.
5704.3Container and portable tank storage. Storage of flammable and combustible liquids in closed containers that do not exceed 60 gallons (227 L) in individual capacity and portable tanks that do not exceed 660 gallons (2498 L) in individual capacity, and limited transfers incidental thereto, shall comply with Sections 5704.3.1 through 5704.3.8.5. | 5704.3 Container and portable tank storage. Storage of flammable and combustible liquids in closed containers that do not exceed 60 gallons (227 L) in individual capacity and portable tanks that do not exceed 660 gallons (2498 L) in individual capacity, and limited transfers incidental thereto, shall comply with Sections 5704.3.1 through 5704.3.8.4.
5704.3.3.5Shelf storage. Shelving shall be of approved construction, adequately braced and anchored. Seismic requirements shall be in accordance with the International Building Code. | (N)5704.3.3.5 Shelf storage. Shelving shall be maintained in accordance with the applicable building code.
5704.3.3.5.1Use of wood. Wood of at least 1 inch (25 mm) nominal thickness is allowed to be used as shelving, racks, dunnage, scuffboards, floor overlay and similar installations. | (N)5704.3.3.5.1 Use of wood. (Section deleted) (N)5704.3.3.5.2 Displacement protection. (Section deleted)
5704.3.3.6Rack storage. Where storage on racks is allowed elsewhere in this code, a minimum 4-foot-wide (1219 mm) aisle shall be provided between adjacent rack sections and any adjacent storage of liquids. Main aisles shall be a minimum of 8 feet (2438 mm) wide. | (N)5704.3.3.6 Rack storage. (Section deleted)
5704.3.4Quantity limits for storage. Liquid storage quantity limitations shall comply with Sections 5704.3.4.1 through 5704.3.4.4. | (N)5704.3.4 Quantity limits for storage. Liquid storage quantity limitations shall be maintained in accordance with the applicable building code.
5704.3.4.1Maximum allowable quantity per control area. For occupancies other than Group M wholesale and retail sales uses, indoor storage of flammable and combustible liquids shall not exceed the maximum allowable quantities per control area indicated in Table 5003.1.1(1) and shall not exceed the additional limitations set forth in this section. For Group M occupancy wholesale and retail sales uses, indoor storage of flammable and combustible liquids shall not exceed the maximum allowable quantities per control area indicated in Table 5704.3.4.1. Storage of hazardous production material flammable and combustible liquids in Group H-5 occupancies shall be in accordance with Chapter 27. | (N)5704.3.4.1 Maximum allowable quantity per control area. (Section deleted)
TABLE 5704.3.4.1 MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA OF FLAMMABLE AND COMBUSTIBLE LIQUIDS IN WHOLESALE AND RETAIL SALES OCCUPANCIESa | (N)TABLE 5704.3.4.1 MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA OF FLAMMABLE AND COMBUSTIBLE LIQUIDS IN WHOLESALE AND RETAIL SALES OCCUPANCIES. (Section deleted)
5704.3.4.2Occupancy quantity limits. The following limits for quantities of stored flammable or combustible liquids shall not be exceeded: 1.Group A occupancies: Quantities in Group A occupancies shall not exceed that necessary for demonstration, treatment, laboratory work, maintenance purposes and operation of equipment, and shall not exceed quantities set forth in Table 5003.1.1(1). 2.Group B occupancies: Quantities in drinking, dining, office and school uses within Group B occupancies shall not exceed that necessary for demonstration, treatment, laboratory work, maintenance purposes and operation of equipment, and shall not exceed quantities set forth in Table 5003.1.1(1). 3.Group E occupancies: Quantities in Group E occupancies shall not exceed that necessary for demonstration, treatment, laboratory work, maintenance purposes and operation of equipment, and shall not exceed quantities set forth in Table 5003.1.1(1). 4.Group F occupancies: Quantities in dining, office, and school uses within Group F occupancies shall not exceed that necessary for demonstration, laboratory work, maintenance purposes and operation of equipment, and shall not exceed quantities set forth in Table 5003.1.1(1). 5.Group I occupancies: Quantities in Group I occupancies shall not exceed that necessary for demonstration, laboratory work, maintenance purposes and operation of equipment, and shall not exceed quantities set forth in Table 5003.1.1(1). 6.Group M occupancies: Quantities in dining, office, and school uses within Group M occupancies shall not exceed that necessary for demonstration, laboratory work, maintenance purposes and operation of equipment, and shall not exceed quantities set forth in Table 5003.1.1(1). The maximum allowable quantities for storage in wholesale and retail sales areas shall be in accordance with Section 5704.3.4.1. 7.Group R occupancies: Quantities in Group R occupancies shall not exceed that necessary for maintenance purposes and operation of equipment, and shall not exceed quantities set forth in Table 5003.1.1(1). 8.Group S occupancies: Quantities in dining and office uses within Group S occupancies shall not exceed that necessary for demonstration, laboratory work, maintenance purposes and operation of equipment, and shall not exceed quantities set forth in Table 5003.1.1(1). 5704.3.4.3Quantities exceeding limits for control areas. Quantities exceeding those allowed in control areas set forth in Section 5704.3.4.1 shall be in liquid storage rooms or liquid storage warehouses in accordance with Sections 5704.3.7 and 5704.3.8. 5704.3.4.4Liquids for maintenance and operation of equipment. In all occupancies, quantities of flammable and combustible liquids in excess of 10 gallons (38 L) used for maintenance purposes and the operation of equipment shall be stored in liquid storage cabinets in accordance with Section 5704.3.2. Quantities not exceeding 10 gallons (38 L) are allowed to be stored outside of a cabinet when in approved containers located in private garages or other approved locations. | (N)5704.3.4.2 Occupancy quantity limits. (Section deleted) (N)5704.3.4.3 Quantities exceeding limits for control areas. (Section deleted)
5704.3.5Storage in control areas. Storage of flammable and combustible liquids in control areas shall be in accordance with Sections 5704.3.5.1 through 5704.3.5.4. | (N)5704.3.5 Storage in control areas. Storage of flammable and combustible liquids in control areas shall be maintained in accordance with the applicable building code.
5704.3.5.1Basement storage. Class I liquids shall be allowed to be stored in basements in amounts not exceeding the maximum allowable quantity per control area for use-open systems in Table 5003.1.1(1), provided that automatic suppression and other fire protection are provided in accordance with Chapter 9. Class II and IIIA liquids shall also be allowed to be stored in basements, provided that automatic suppression and other fire protection are provided in accordance with Chapter 9. | (N)5704.3.5.1 Basement storage. (Section deleted)
5704.3.6.2Container capacity. Containers for Class I liquids shall not exceed a capacity of 5 gallons (19 L). Exception: Metal containers not exceeding 55 gallons (208 L) are allowed to store up to 240 gallons (908 L) of the maximum allowable quantity per control area of Class IB and IC liquids in a control area. The building shall be equipped throughout with an approved automatic sprinkler system in accordance with Table 5704.3.4.1. The containers shall be provided with plastic caps without cap seals and shall be stored upright. Containers shall not be stacked or stored in racks and shall not be located in areas accessible to the public. | 5704.3.6.2 Container capacity. Containers for Class I liquids shall not exceed a capacity of 5 gallons (19 L). Exception: Metal containers not exceeding 55 gallons (208 L) are allowed to store up to 240 gallons (908 L) of the maximum allowable quantity per control area of Classes IB and IC liquids in a control area. The building shall be equipped throughout with an approved automatic sprinkler system in accordance with the applicable building code. The containers shall be provided with plastic caps without cap seals and shall be stored upright. Containers shall not be stacked or stored in racks and shall not be located in areas accessible to the public.
5704.3.7.1General. Quantities of liquids exceeding those set forth in Section 5704.3.4.1 for storage in control areas shall be stored in a liquid storage room complying with this section and constructed and separated as required by the International Building Code. | (N)5704.3.7.1 General. Quantities of liquids exceeding those set forth in the applicable building code for storage in control areas shall be stored in a liquid storage room complying with the applicable building code.
5704.3.7.2.2Separation and aisles. Piles shall be separated from each other by at least 4-foot (1219 mm) aisles. Aisles shall be provided so that all containers are 20 feet (6096 mm) or less from an aisle. Where the storage of liquids is on racks, a minimum 4-foot-wide (1219 mm) aisle shall be provided between adjacent rows of racks and adjacent storage of liquids. Main aisles shall be a minimum of 8 feet (2438 mm) wide. Additional aisles shall be provided for access to doors, required windows and ventilation openings, standpipe connections, mechanical equipment and switches. Such aisles shall be at least 3 feet (914 mm) in width, unless greater widths are required for separation of piles or racks, in which case the greater width shall be provided. | (N)5704.3.7.2.2 Separation and aisles. Piles shall be separated from each other in accordance with the applicable building code. Aisles shall be maintained in accordance with the applicable building code.
5704.3.7.3Spill control and secondary containment. Liquid storage rooms shall be provided with spill control and secondary containment in accordance with Section 5004.2. 5704.3.7.4Ventilation. Liquid storage rooms shall be ventilated in accordance with Section 5004.3. 5704.3.7.5Fire protection. Fire protection for liquid storage rooms shall comply with Sections 5704.3.7.5.1 and 5704.3.7.5.2. | (N)5704.3.7.3 Spill control and secondary containment. Liquid storage rooms shall be maintained in accordance with the applicable building code. (N)5704.3.7.4 Ventilation. Ventilation for storage rooms shall be maintained in accordance with the applicable building code. (N)5704.3.7.5 Fire protection. Fire protection for liquid storage rooms shall be maintained in accordance with the applicable building code.
5704.3.7.5.1Fire-extinguishing systems. Liquid storage rooms shall be protected by automatic sprinkler systems installed in accordance with Chapter 9 and Tables 5704.3.6.3(4) through 5704.3.6.3(7) and Table 5704.3.7.5.1. In-rack sprinklers shall also comply with NFPA 13. Automatic foam-water systems and automatic aqueous film-forming foam (AFFF) water sprinkler systems shall not be used except when approved. Protection criteria developed from fire modeling or full-scale fire testing conducted at an approved testing laboratory are allowed in lieu of the protection as shown in Tables 5704.3.6.3(2) through 5704.3.6.3(7) and Table 5704.3.7.5.1 when approved. | (N)5704.3.7.5.1 Fire-extinguishing systems. (Section deleted)
5704.3.8Liquid storage warehouses. Buildings used for storage of flammable or combustible liquids in quantities exceeding those set forth in Section 5704.3.4 for control areas and Section 5704.3.7 for liquid storage rooms shall comply with Sections 5704.3.8.1 through 5704.3.8.5 and shall be constructed and separated as required by the International Building Code. | (N)5704.3.8 Liquid storage warehouses. Liquid storage warehouses shall be maintained in accordance with the applicable building code. (N)5704.3.8.1 Quantities and storage arrangement. The total quantities of liquids in a liquid storage warehouse shall be maintained in accordance with the applicable building code. The arrangement of storage shall be in accordance with Table 5704.3.6.3(2) or 5704.3.6.3(3).
5704.3.8.1.1Mixed storage. Mixed storage shall be in accordance with Section 5704.3.7.2.1. 5704.3.8.1.2Separation and aisles. Separation and aisles shall be in accordance with Section 5704.3.7.2.2. | (N)5704.3.8.1.1 Mixed storage. (Section deleted) (N)5704.3.8.1.2 Separation and aisles. (Section deleted)
5704.3.8.2Spill control and secondary containment. Liquid storage warehouses shall be provided with spill control and secondary containment as set forth in Section 5004.2. 5704.3.8.3Ventilation. Liquid storage warehouses storing containers greater than 5 gallons (19 L) in capacity shall be ventilated at a rate of not less than 0.25 cfm per square foot (0.075 m3/s • m2) of floor area over the storage area. 5704.3.8.4Fire-extinguishing systems. Liquid storage warehouses shall be protected by automatic sprinkler systems installed in accordance with Chapter 9 and Tables 5704.3.6.3(4) through 5704.3.6.3(7) and Table 5704.3.7.5.1, or Sections 16.4.1 through 16.4.3, 16.5.1 through 16.5.2.12, and Tables 16.5.2.1 through 16.5.2.12 and Figures 16.4.1(a) through 16.4.1(c) of NFPA 30. In-rack sprinklers shall also comply with NFPA 13. Automatic foam-water systems and automatic AFFF water sprinkler systems shall not be used except where approved. Protection criteria developed from fire modeling or full-scale fire testing conducted at an approved testing laboratory are allowed in lieu of the protection as shown in Tables 5704.3.6.3(2) through 5704.3.6.3(7) and Table 5704.3.7.5.1 where approved. | (N)5704.3.8.2 Spill control and secondary containment. Spill control and secondary containment for liquid storage warehouses shall be maintained in accordance with the applicable building code. (N)5704.3.8.3 Ventilation. Ventilation for liquid storage warehouses storing containers greater than 5 gallons (19 L) in capacity shall be maintained in accordance with the applicable building code. (N)5704.3.8.4 Automatic sprinkler systems. Automatic sprinkler systems for storage warehouses shall be maintained in accordance with the applicable building code.
5704.3.8.5Warehouse hose lines. In liquid storage warehouses, either 11/2-inch (38 mm) lined or 1-inch (25 mm) hard rubber hand hose lines shall be provided in sufficient number to reach all liquid storage areas and shall be in accordance with Section 903 or Section 905. | (N)5704.3.8.5 Warehouse hose lines. (Section deleted)
5704.4.3Spill control and secondary containment. Storage areas shall be provided with spill control and secondary containment in accordance with Section 5703.4. Exception: Containers stored on approved containment pallets in accordance with Section 5004.2.3 and containers stored in cabinets and lockers with integral spill containment. | (N)5704.4.3 Spill control and secondary containment. Spill control and secondary containment for storage areas shall be maintained in accordance with the applicable building code.
5704.4.7Weather protection. Weather protection for outdoor storage shall be in accordance with Section 5004.13. | (N)5704.4.7 Weather protection. (Section deleted)
5705.3.6.2.3Solvent quantity limits. Solvent quantities shall be limited as follows: 1.Machines without remote solvent reservoirs shall be limited to quantities set forth in Section 5705.3.5. 2.Machines with remote solvent reservoirs using Class I liquids shall be limited to quantities set forth in Section 5705.3.5. 3.Machines with remote solvent reservoirs using Class II liquids shall be limited to 35 gallons (132 L) per machine. The total quantities shall not exceed an aggregate of 240 gallons (908 L) per control area in buildings not equipped throughout with an approved automatic sprinkler system and an aggregate of 480 gallons (1817 L) per control area in buildings equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1. 4.Machines with remote solvent reservoirs using Class IIIA liquids shall be limited to 80 gallons (303 L) per machine. | 5705.3.6.2.3 Solvent quantity limits. Solvent quantities shall be limited as follows: 1. Machines without remote solvent reservoirs shall be limited to quantities set forth in Section 5705.3.5. 2. Machines with remote solvent reservoirs using Class I liquids shall be limited to quantities set forth in Section 5705.3.5. 3. Machines with remote solvent reservoirs using Class II liquids shall be limited to 35 gallons (132 L) per machine. The total quantities shall not exceed an aggregate of 240 gallons (908 L) per control area in buildings not equipped throughout with an approved automatic sprinkler system and an aggregate of 480 gallons (1817 L) per control area in buildings equipped throughout with an approved automatic sprinkler system in accordance the applicable building code. 4. Machines with remote solvent reservoirs using Class IIIA liquids shall be limited to 80 gallons (303 L) per machine.
5705.5Alcohol-based hand rubs classified as Class I or II liquids. The use of wall-mounted dispensers containing alcohol-based hand rubs classified as Class I or II liquids shall be in accordance with all of the following: 1.The maximum capacity of each dispenser shall be 68 ounces (2 L). 2.The minimum separation between dispensers shall be 48 inches (1219 mm). 3.The dispensers shall not be installed directly adjacent to, directly above or below an electrical receptacle, switch, appliance, device or other ignition source. The wall space between the dispenser and the floor shall remain clear and unobstructed. 4.Dispensers shall be mounted so that the bottom of the dispenser is a minimum of 42 inches (1067 mm) and a maximum of 48 inches (1219 mm) above the finished floor. 5.Dispensers shall not release their contents except when the dispenser is manually activated. Facilities shall be permitted to install and use automatically activated “touch free” alcohol-based hand-rub dispensing devices with the following requirements: 5.1.The facility or persons responsible for the dispensers shall test the dispensers each time a new refill is installed in accordance with the manufacturer’s care and use instructions. 5.2.Dispensers shall be designed and must operate in a manner that ensures accidental or malicious activations of the dispensing device are minimized. At a minimum, all devices subject to or used in accordance with this section shall have the following safety features: 5.2.1.Any activations of the dispenser shall only occur when an object is placed within 4 inches (98 mm) of the sensing device. 5.2.2.The dispenser shall not dispense more than the amount required for hand hygiene consistent with label instructions as regulated by the United States Food and Drug Administration (USFDA). 5.2.3.An object placed within the activation zone and left in place will cause only one activation. 6.Storage and use of alcohol-based hand rubs shall be in accordance with the applicable provisions of Sections 5704 and 5705. 7.Dispensers installed in occupancies with carpeted floors shall only be allowed in smoke compartments or fire areas equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. | 5705.5 Alcohol-based hand rubs classified as Class I or II liquids. The use of wallmounted dispensers containing alcoholbased hand rubs classified as Class I or II liquids shall be in accordance with all of the following: 1. The maximum capacity of each dispenser shall be 68 ounces (2 L). 2. The minimum separation between dispensers shall be 48 inches (1219 mm). 3. The dispensers shall not be installed above, below, or closer than 1 inch (25 mm) to an electrical receptacle, switch, appliance, device or other ignition source. The wall space between the dispenser and the floor or intervening countertop shall be free of electrical receptacles, switches, appliances, devices or other ignition sources. 4. Dispensers shall be mounted so that the bottom of the dispenser is not less than 42 inches (1067 mm) and not more than 48 inches (1219 mm) above the finished floor. 5. Dispensers shall not release their contents except when the dispenser is manually activated. Facilities shall be permitted to install and use automatically activated "touch free" alcohol-based hand-rub dispensing devices with the following requirements: 5.1. The facility or persons responsible for the dispensers shall test the dispensers each time a new refill is installed in accordance with the manufacturer's care and use instructions. 5.2. Dispensers shall be designed and must operate in a manner that ensures accidental or malicious activations of the dispensing device are minimized. At a minimum, all devices subject to or used in accordance with this section shall have the following safety features: 5.2.1. Any activations of the dispenser shall only occur when an object is placed within 4 inches (98 mm) of the sensing device. 5.2.2. The dispenser shall not dispense more than the amount required for hand hygiene consistent with label instructions as regulated by the U.S. Food and Drug Administration (USFDA). 5.2.3. An object placed within the activation zone and left in place will cause only one activation 6. Storage and use of alcohol-based hand rubs shall be in accordance with the applicable provisions of Sections 5704 and 5705. 7. Dispensers installed in occupancies with carpeted floors shall only be allowed in smoke compartments or fire areas equipped throughout with an approved automatic sprinkler system in accordance with the applicable building code.
5705.5.1Corridor installations. Where wall-mounted dispensers containing alcohol-based hand rubs are installed in corridors, they shall be in accordance with all of the following: 1.Level 2 and 3 aerosol containers shall not be allowed in corridors. 2.The maximum capacity of each Class I or II liquid dispenser shall be 41 ounces (1.21 L) and the maximum capacity of each Level 1 aerosol dispenser shall be 18 ounces (0.51 kg). 3.The maximum quantity allowed in a corridor within a control area shall be 10 gallons (37.85 L) of Class I or II liquids or 1135 ounces (32.2 kg) of Level 1 aerosols, or a combination of Class I or II liquids and Level 1 aerosols not to exceed, in total, the equivalent of 10 gallons (37.85 L) or 1,135 ounces (32.2 kg) such that the sum of the ratios of the liquid and aerosol quantities divided by the allowable quantity of liquids and aerosols, respectively, shall not exceed one. 4.The minimum corridor width shall be 72 inches (1829 mm). 5.Projections into a corridor shall be in accordance with Section 1003.3.3. | (N)5705.5.1 Corridor installations. (Section deleted)
None | 5706.1.1 Mobile fueling operations. Delivery of Class I, Class II, and Class III liquids to the fuel tank of a highway vehicle from a tank vehicle, a tank carried on a vehicle, or a nonportable container is prohibited. Exceptions: 1. The refueling of highway vehicles in an emergency. 2. The refueling of vehicles in compliance with Sections 5706.5.4.1 through 5706.5.4.5. 3. Vehicles used for farm operations and machinery.
5706.2.4.2Vents. Tanks shall be provided with a method of normal and emergency venting. Normal vents shall also be in accordance with Section 5704.2.7.3. Emergency vents shall be in accordance with Section 5704.2.7.4. Emergency vents shall be arranged to discharge in a manner which prevents localized overheating or flame impingement on any part of the tank in the event that vapors from such vents are ignited. | 5706.2.4.2 Vents. Tanks shall be provided with a method of normal and emergency venting. Normal vents shall be in accordance with the applicable building code. Emergency vents shall be in accordance with Section 5704.2.7.4. Emergency vents shall be arranged to discharge in a manner that prevents localized overheating or flame impingement on any part of the tank in the event that vapors from such vents are ignited.
5706.2.6Spill control drainage control and diking. Indoor storage and dispensing areas shall be provided with spill control and drainage control as set forth in Section 5703.4. Outdoor storage areas shall be provided with drainage control or diking as set forth in Section 5704.2.10. | (N)5706.2.6 Spill control drainage control and diking. Outdoor storage areas shall be provided with drainage control or diking as set forth in the applicable building code.
5706.3.3Sumps. Sumps associated with wells shall comply with Sections 5706.3.3.1 through 5706.3.3.3. | (N)5706.3.3 Sumps. Sumps associated with wells shall be maintained in accordance with the applicable building code.
5706.3.3.1Maximum width. Sumps or other basins for the retention of oil or petroleum products shall not exceed 12 feet (3658 mm) in width. | (N)5706.3.3.1 Maximum width. (Section deleted)
5706.3.3.3Security. Sumps, diversion ditches and depressions used as sumps shall be securely fenced or covered. | (N)5706.3.3.3 Security. (Section deleted)
5706.4.1Building construction. Buildings shall be constructed in accordance with the International Building Code. 5706.4.2Means of egress. Rooms in which liquids are stored, used or transferred by pumps shall have means of egress arranged to prevent occupants from being trapped in the event of fire. | (N)5706.4.1 Building construction. Buildings shall be maintained in accordance with the applicable building code. (N)5706.4.2 Means of egress. Means of egress from rooms in which liquids are stored, used or transferred by pumps shall be maintained in accordance with the applicable building code.
5706.4.4Ventilation. Ventilation shall be provided for rooms, buildings and enclosures in which Class I liquids are pumped, used or transferred. Design of ventilation systems shall consider the relatively high specific gravity of the vapors. When natural ventilation is used, adequate openings in outside walls at floor level, unobstructed except by louvers or coarse screens, shall be provided. When natural ventilation is inadequate, mechanical ventilation shall be provided in accordance with the International Mechanical Code. | (N)5706.4.4 Ventilation. Ventilation for rooms, buildings and enclosures in which Class I liquids are pumped, used or transferred shall be maintained in accordance with the applicable building code. (N)5706.4.7.6 Piping, valves and fittings. Piping, valves and fittings shall be maintained in accordance with the applicable building code. (N)5706.4.9 Drainage control. Loading and unloading areas shall be provided with drainage control in accordance with the applicable building code.
5706.4.6Overfill protection of Class I and II liquids. Manual and automatic systems shall be provided to prevent overfill during the transfer of Class I and II liquids from mainline pipelines and marine vessels in accordance with API 2350. | (N)5706.4.7.6 Piping, valves and fittings. Piping, valves and fittings shall be maintained in accordance with the applicable building code.
5706.4.9Drainage control. Loading and unloading areas shall be provided with drainage control in accordance with Section 5704.2.10. | (N)5706.4.9 Drainage control. Loading and unloading areas shall be provided with drainage control in accordance with the applicable building code.
5706.4.10Fire protection. Fire protection shall be in accordance with Chapter 9 and Sections 5706.4.10.1 through 5706.4.10.4. | (N)5706.4.10 Fire protection. Fire protection for bulk plants or terminals shall be maintained in accordance with the applicable building code.
5706.5.1.2Weather protection canopies. Where weather protection canopies are provided, they shall be constructed in accordance with Section 5004.13. Weather protection canopies shall not be located within 15 feet (4572 mm) of a building or combustible material or within 25 feet (7620 mm) of building openings, lot lines , public streets, public alleys or public ways. 5706.5.1.3Ventilation. Ventilation shall be provided to prevent accumulation of vapors in accordance with Section 5705.3.7.5.1. | (N)5706.5.1.2 Weather protection canopies. Where weather protection canopies are provided, they shall be maintained in accordance with the applicable building code. (N)5706.5.1.3 Ventilation. Ventilation shall be maintained in accordance with the applicable building code.
5706.5.1.5Spill control and secondary containment. Areas where transfer operations are located shall be provided with spill control and secondary containment in accordance with Section 5703.4. The spill control and secondary containment system shall have a design capacity capable of containing the capacity of the largest tank compartment located in the area where transfer operations are conducted. Containment of the rainfall volume specified in Section 5004.2.2.6 is not required. 5706.5.1.6Fire protection. Fire protection shall be in accordance with Section 5703.2. | (N)5706.5.1.5 Spill control and secondary containment. The spill control and secondary containment system shall be maintained in accordance with the applicable building code. (N)5706.5.1.6 Fire protection. Fire protection shall be maintained in accordance with the applicable building code.
5706.8.1Over-pressure/vacuum protection. Tanks and equipment shall have independent venting for over-pressure or vacuum conditions that might occur from malfunction of the vapor recovery or processing system. Exception: For tanks, venting shall comply with Section 5704.2.7.3. | 5706.8.1 Over-pressure or vacuum protection. Tanks and equipment shall have independent venting for over-pressure or vacuum conditions that might occur from malfunction of the vapor recovery or processing system. Exception: For tanks, venting shall comply with the applicable building code.
5706.8.3Vapor collection systems and overfill protection. The design and operation of the vapor collection system and overfill protection shall be in accordance with this section and Section 19.5 of NFPA 30. | 5706.8.3 Vapor collection systems and overfill protection. The operation of the vapor collection system and overfill protection shall be in accordance with this section and Section 19.5 of NFPA 30.
5706.8.5Overfill protection. Storage tanks served by vapor recovery or processing systems shall be equipped with overfill protection in accordance with Section 5704.2.7.5.8. | 5706.8.5 Overfill protection. Storage tanks served by vapor recovery or processing systems shall be equipped with overfill protection in accordance with the applicable building code.

## Ch58 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
5801.1Scope. The storage and use of flammable gases and flammable cryogenic fluids shall be in accordance with this chapter and NFPA 55. Compressed gases shall also comply with Chapter 53 and cryogenic fluids shall also comply with Chapter 55. Flammable cryogenic fluids shall comply with Section 5806. Hydrogen motor fuel-dispensing stations and repair garages and their associated above-ground hydrogen storage systems shall also be designed and constructed in accordance with Chapter 23. Exceptions: 1.Gases used as refrigerants in refrigeration systems (see Section 606). 2.Liquefied petroleum gases and natural gases regulated by Chapter 61. 3.Fuel-gas systems and appliances regulated under the International Fuel Gas Code other than gaseous hydrogen systems and appliances. 4.Pyrophoric gases in accordance with Chapter 64. 5801.2Permits. Permits shall be required as set forth in Section 107.2. | (N)5801.1 Scope. The storage and use of flammable gases and flammable cryogenic fluids shall be in accordance with this chapter and NFPA 55. Compressed gases shall also comply with Chapter 53 and cryogenic fluids shall also comply with Chapter 55. Flammable cryogenic fluids shall comply with Section 5806. Hydrogen motor fueldispensing stations and repair garages and their associated aboveground hydrogen storage systems shall also be designed, constructed and maintained in accordance with Chapter 23 and NFPA 2. Exceptions: 1. Gases used as refrigerants in refrigeration systems (see Section 606). 2. Liquefied petroleum gases and natural gases regulated by Chapter 61. 3. Fuel-gas systems and appliances regulated under the International Fuel Gas Code other than gaseous hydrogen systems and appliances. 4. Pyrophoric gases in accordance with Chapter 64. 5801.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | No change
5803.1Quantities not exceeding the maximum allowable quantity per control area. The storage and use of flammable gases in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with Sections 5001, 5003, 5801 and 5803. | (N)5803.1 Quantities not exceeding the maximum allowable quantity per control area. The storage and use of flammable gases in amounts not exceeding the maximum allowable quantity per control area under the applicable building code. |  |  | 5803.1Quantities not exceeding the maximum allowable quantity per control area. The storage and use of flammable gases in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be maintained in accordance with Sections 5001, 5003, 5801 and 5803.
5803.1.1.2Aggregate quantity. The aggregate quantities of flammable gases used for maintenance purposes and operation of equipment shall not exceed the maximum allowable quantity per control area indicated in Table 5003.1.1(1). | (N)5803.1.1.2 Aggregate quantity. The aggregate quantities of flammable gases used for maintenance purposes and operation of equipment shall not exceed the maximum allowable quantity per control area under the applicable building code. |  |  | 5803.1.1.2Aggregate quantity. The aggregate quantities of flammable gases used for maintenance purposes and operation of equipment shall be maintained as to not exceed the maximum allowable quantity per control area indicated in Table 5003.1.1(1) unless otherwise approved by the applicable buliding code.
5803.1.5Electrical. Electrical wiring and equipment shall be installed and maintained in accordance with Section 605 and NFPA 70. | (N)5803.1.5 Electrical. Electrical wiring and equipment shall be maintained in accordance with the applicable building code. |  |  | 5803.1.5Electrical. Electrical wiring and equipment shall be maintained in accordance with Chapter 6 and NFPA 70.
5804.1Indoor storage. Indoor storage of flammable gases in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1), shall be in accordance with Sections 5001, 5003 and 5004, and this chapter. | (N)5804.1 Indoor storage. Indoor storage of flammable gases in amounts exceeding the maximum allowable quantity per control area in accordance with the applicable building code and this chapter. |  |  | 5804.1Indoor storage. Indoor storage of flammable gases in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1), shall be maintained in accordance with Sections 5001, 5003 and 5004, and this chapter and approved in accordance with the applicable building code.
5804.1.1Explosion control. Buildings or portions thereof containing flammable gases shall be provided with explosion control in accordance with Section 911. | (N)5804.1.1 Explosion control. (Section deleted) |  |  | 5804.1.1Explosion control. Buildings or portions thereof containing flammable gases and provided with explosion control shall be maintained in accordance with Section 911 and remain in accordance with the applicable building code.
5806.2Limitations. Storage of flammable cryogenic fluids in stationary containers outside of buildings is prohibited within the limits established by law as the limits of districts in which such storage is prohibited (see Section 3 of the Sample Legislation for Adoption of the International Fire Code on page xxi). | (N)5806.2 Limitations. (Section deleted) |  | Consider reference to the applicable building code and local ordiances. | 5806.2Limitations. Storage of flammable cryogenic fluids in stationary containers outside of buildings is prohibited within the limits established by law as the limits of districts in which such storage is prohibited (see Section 3 of the Sample Legislation for Adoption of the International Fire Code on page xxi).
5806.3Above-ground tanks for liquid hydrogen. Above-ground tanks for the storage of liquid hydrogen shall be in accordance with Sections 5806.3 through 5806.3.2.1. | (N)5806.3 Aboveground tanks for liquid hydrogen. Aboveground tanks for the storage of liquid hydrogen shall be maintained in accordance with the applicable building code. |  | ...shall be maintained in accordance with this chapter and remain as approved in accordance with the applicable building code. | No change
5806.3.1Construction of the inner vessel. The inner vessel of storage tanks in liquid hydrogen service shall be designed and constructed in accordance with Section VIII, Division 1, of the ASME Boiler and Pressure Vessel Code and shall be vacuum jacketed in accordance with Section 5806.3.2. | (N)5806.3.1 Construction of the inner vessel. (Section deleted) (N)5806.3.2 Construction of the vacuum jacket (outer vessel). (Section deleted) (N)5806.3.2.1 Vacuum-level monitoring. (Section deleted) |  |  | No change
5806.4Underground tanks for liquid hydrogen. Underground tanks for the storage of liquid hydrogen shall be in accordance with Sections 5806.4.1 through 5806.4.8.3. | (N)5806.4 Underground tanks for liquid hydrogen. Underground tanks for the storage of liquid hydrogen shall be maintained in accordance with the applicable building code. |  |  | No change
5806.4.1Construction. Storage tanks for liquid hydrogen shall be designed and constructed in accordance with ASME Boiler and Pressure Vessel Code (Section VIII, Division 1) and shall be vacuum jacketed in accordance with Section 5806.4.8. 5806.4.2Location. Storage tanks shall be located outside in accordance with the following: 1.Tanks and associated equipment shall be located with respect to foundations and supports of other structures such that the loads carried by the latter cannot be transmitted to the tank. 2.The distance from any part of the tank to the nearest wall of a basement, pit, cellar or lot line shall not be less than 3 feet (914 mm). 3.A minimum distance of 1 foot (305 mm), shell to shell, shall be maintained between underground tanks. 5806.4.3Depth, cover and fill. The tank shall be buried such that the top of the vacuum jacket is covered with a minimum of 1 foot (305 mm) of earth and with concrete a minimum of 4 inches (102 mm) thick placed over the earthen cover. The concrete shall extend a minimum of 1 foot (305 mm) horizontally beyond the footprint of the tank in all directions. Underground tanks shall be set on firm foundations constructed in accordance with the International Building Code and surrounded with at least 6 inches (152 mm) of noncorrosive inert material, such as sand. Exception: The vertical extension of the vacuum jacket as required for service connections. | (N)5806.4.1 Construction. (Section deleted) (N)5806.4.2 Location. (Section deleted) (N)5806.4.3 Depth, cover and fill. (Section deleted) |  |  | No change
5806.4.4Anchorage and security. Tanks and systems shall be secured against accidental dislodgement in accordance with this chapter. | (N)5806.4.4 Anchorage and security. Anchorage provided for tanks and systems shall be maintained in accordance with the applicable building code. |  | maintenance language? | No change
5806.4.5Venting of underground tanks. Vent pipes for underground storage tanks shall be in accordance with Section 5503.3. 5806.4.6Underground liquid hydrogen piping. Underground liquid hydrogen piping shall be vacuum jacketed or protected by approved means and designed in accordance with Chapter 55. 5806.4.7Overfill protection and prevention systems. An approved means or method shall be provided to prevent the overfill of all storage tanks. 5806.4.8Vacuum jacket construction. The vacuum jacket shall be designed and constructed in accordance with Section VIII of ASME Boiler and Pressure Vessel Code and shall be designed to withstand the anticipated loading, including loading from vehicular traffic, where applicable. Portions of the vacuum jacket installed below grade shall be designed to withstand anticipated soil, seismic and hydrostatic loading. 5806.4.8.1Material. The vacuum jacket shall be constructed of stainless steel or other approved corrosion-resistant material. 5806.4.8.2Corrosion protection. The vacuum jacket shall be protected by approved or listed corrosion-resistant materials or an engineered cathodic protection system. Where cathodic protection is utilized, an approved maintenance schedule shall be established. Exposed components shall be inspected at least twice a year. Maintenance and inspection events shall be recorded and those records shall be maintained on the premises for a minimum of three years and made available to the fire code official upon request. 5806.4.8.3Vacuum-level monitoring. An approved method shall be provided to indicate loss of vacuum within the vacuum jacket(s). | (N)5806.4.5 Venting of underground tanks. (Section deleted) (N)5806.4.6 Underground liquid hydrogen piping. (Section deleted) (N)5806.4.7 Overfill protection and prevention systems. (Section deleted) (N)5806.4.8 Vacuum jacket construction. (Section deleted) (N)5806.4.8.1 Material. (Section deleted) (N)5806.4.8.2 Corrosion protection. (Section deleted) (N)5806.4.8.3 Vacuum-level monitoring. (Section deleted) |  |  | No change
5807.1.10Electrical. Electrical components for metal hydride storage systems shall be designed, constructed and installed in accordance with NFPA 70. | (N)5807.1.10 Electrical. Electrical components for metal hydride storage systems shall be maintained in accordance with NFPA 70. |  |  | (N)5807.1.10 Electrical. Electrical components for metal hydride storage systems shall be maintained in accordance with Chapter 6 and NFPA 70.
None | (N)5808.1 General. Where required by the applicable building code, hydrogen fuel gas rooms shall be maintained. |  | ...shall be maintained in accordace with this chapter and remain in accordance with the applicable building code. | No change
None | (N)5808.2 Location. (Section deleted) (N)5808.3 Design and construction. (Section deleted) (N)5808.3.1 Pressure control. (Section deleted) (N)5808.3.2 Windows. (Section deleted) |  |  | No change
None | (N)5808.4 Exhaust ventilation. Ventilation required for hydrogen fuel gas rooms shall be maintained in accordance with the applicable building code. (N)5808.5 Gas detection system. Gas detection systems required for hydrogen fuel gas rooms shall be maintained in accordance with the applicable building. |  | maintenance and operation language for ventilation? maintenance language for gas detection system as a pointer to 908? | No change
None | (N)5808.5.1 System design. (Section deleted) (N)5808.5.2 Gas detection system components. (Section deleted) (N)5808.5.3 Operation. (Section deleted) (N)5808.5.4 Failure of the gas detection system. (Section deleted) |  |  | (N)5808.5.1 System design. (Section deleted) (N)5808.5.2 Gas detection system components. (Section deleted) (N)5808.5.3 Operation. Where provided, activation of the gas detection system shall be maintained to result in both of the following: 1. Inititation of distinct audible and visual alarm signals both inside and outside of the hydrogen fuel gas room. 2. Activation of the mechanical exhaust ventilation system. (N)5808.5.4 Failure of the gas detection system. Where provided, failure of the gas detection system shall be maintained to result in the activation of the mechanical exhaust ventilation system, cessation of the hydrogen generation and the sounding of a trouble signal in an approved location.
None | (N)5808.6 Explosion control. Explosion control required for hydrogen fuel gas rooms shall be maintained in accordance with the applicable building code. (N)5808.7 Standby power. Standby power provided for mechanical ventilation and gas detection systems shall be maintained in accordance with the applicable building code. |  |  | (N)5808.6 Explosion control. Explosion control required for hydrogen fuel gas rooms shall be maintained in accordance with the applicable building code and Chapter 9 and remain in accordance with the applicable building code. (N)5808.7 Standby power. Standby power provided for mechanical ventilation and gas detection systems shall be maintained in accordance with Chapter 6 and remain in accordance with the applicable building code.

## Ch59 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
5901.2 Permits. Permits shall be required as set forth in Section 107.2. | 5901.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | No change
5904.1 Indoor storage. Indoor storage of flammable solids in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1) shall be in accordance with Sections 5001, 5003, 5004 and this chapter. | (N)5904.1 Indoor storage. Indoor storage of flammable solids in amounts exceeding the maximum allowable quantity per control area shall be in accordance with the applicable building code. |  |  | 5904.1 Indoor storage. Indoor storage of flammable solids in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1) shall be maintained in accordance with Sections 5001, 5003, 5004, this chapter and approved in accordance with the applicable building code.
5904.1.1 Pile size limits and location. Flammable solids stored in quantities greater than 1,000 cubic feet (28 m3) shall be separated into piles each not larger than 1,000 cubic feet (28 m3). | (N)5904.1.1 Pile size limits and location. (Section deleted) |  |  | 5904.1.1 Pile size limits and location. Flammable solids stored in quantities greater than 1,000 cubic feet (28 m3) shall be separated into piles each not larger than 1,000 cubic feet (28 m3).
5904.1.2 Aisles. Aisle widths between piles shall not be less than the height of the piles or 4 feet (1219 mm), whichever is greater. 5904.1.3 Basement storage. Flammable solids shall not be stored in basements. | (N)5904.1.2 Aisles. Aisle widths between piles shall be maintained in accordance with the applicable building code. (N)5904.1.3 Basement storage. Flammable solids shall not be stored in basements unless previously approved. |  |  | 5904.1.2 Aisles. Aisle widths between piles shall be maintained to be not be less than the height of the piles or 4 feet (1219 mm), whichever is greater. 5904.1.3 Basement storage. Flammable solids shall not be stored in basements unless approved in accordance with the applicable building code.
5906.2 Storage of magnesium articles. The storage of magnesium shall comply with Sections 5906.2.1 through 5906.4.3. | (N)5906.2 Storage of magnesium articles. The storage of magnesium shall be maintained in accordance with the applicable building code. |  |  | 5906.2 Storage of magnesium articles. The storage of magnesium shall comply with Sections 5906.2.1 through 5906.4.3.
5906.2.1 Storage of greater than 50 cubic feet. Magnesium storage in quantities greater than 50 cubic feet (1.4 m3) shall be separated from storage of other materials that are either combustible or in combustible containers by aisles. Piles shall be separated by aisles with a minimum width of not less than the pile height. 5906.2.2 Storage of greater than 1,000 cubic feet. Magnesium storage in quantities greater than 1,000 cubic feet (28 m3) shall be separated into piles not larger than 1,000 cubic feet (28 m3) each. Piles shall be separated by aisles with a minimum width of not less than the pile height. Such storage shall not be located in nonsprinklered buildings of Type III, IV or V construction, as defined in the International Building Code. 5906.2.3 Storage in combustible containers or within 30 feet of other combustibles. Where in nonsprinklered buildings of Type III, IV or V construction, as defined in the International Building Code, magnesium shall not be stored in combustible containers or within 30 feet (9144 mm) of other combustibles. | (N)5906.2.1 Storage of greater than 50 cubic feet. (Section deleted) (N)5906.2.2 Storage of greater than 1,000 cubic feet. (Section deleted) (N)5906.2.3 Storage in combustible containers or within 30 feet of other combustibles. (Section deleted) |  |  | 5906.2.1 Storage of greater than 50 cubic feet. Magnesium storage in quantities greater than 50 cubic feet (1.4 m3) shall be separated from storage of other materials that are either combustible or in combustible containers by aisles. Piles shall be separated by aisles with a minimum width of not less than the pile height. 5906.2.2 Storage of greater than 1,000 cubic feet. Magnesium storage in quantities greater than 1,000 cubic feet (28 m3) shall be separated into piles not larger than 1,000 cubic feet (28 m3) each. Piles shall be separated by aisles with a minimum width of not less than the pile height. Unless approved by the applicable building code, such storage shall not be located in nonsprinklered buildings of Type III, IV or V construction, as defined in the applicalbe building code. 5906.2.3 Storage in combustible containers or within 30 feet of other combustibles. Where storerd in nonsprinklered buildings of Type III, IV or V construction as defined in the applicalbe building code, magnesium shall not be stored in combustible containers or within 30 feet (9144 mm) of other combustibles.
5906.3.1 Indoor storage. Indoor storage of pigs, ingots and billets shall only be on floors of noncombustible construction. Piles shall not be larger than 500,000 pounds (226.8 metric tons) each. Piles shall be separated by aisles with a minimum width of not less than one-half the pile height. | (N)5906.3.1 Indoor storage. Indoor storage of pigs, ingots and billets shall be maintained in accordance with the applicable building code. |  |  | 5906.3.1 Indoor storage. Indoor storage of pigs, ingots and billets shall only be on floors of noncombustible construction. Piles shall not be larger than 500,000 pounds (226.8 metric tons) each. Piles shall be separated by aisles with a minimum width of not less than one-half the pile height.
5906.4 Storage of fine magnesium scrap. The storage of scrap magnesium shall comply with Sections 5906.4.1 through 5906.4.3. | (N)5906.4 Storage of fine magnesium scrap. The storage of scrap magnesium shall be maintained in accordance with the applicable building code. |  |  | 5906.4 Storage of fine magnesium scrap. The storage of scrap magnesium shall comply with Sections 5906.4.1 through 5906.4.3.
5906.4.2 Storage of 50 to 1,000 cubic feet. Storage of fine magnesium scrap in quantities greater than 50 cubic feet (1.4 m3) [six 55-gallon (208 L) steel drums] shall be separated from other occupancies by an open space of at least 50 feet (15 240 mm) or by a fire barrier constructed in accordance with Section 707 of the International Building Code. 5906.4.3 Storage of greater than 1,000 cubic feet. Storage of fine magnesium scrap in quantities greater than 1,000 cubic feet (28 m3) shall be separated from all buildings other than those used for magnesium scrap recovery operations by a distance of not less than 100 feet (30 480 mm). | (N)5906.4.2 Storage of 50 to 1,000 cubic feet. (Section deleted) (N)5906.4.3 Storage of greater than 1,000 cubic feet. (Section deleted) |  |  | 5906.4.2 Storage of 50 to 1,000 cubic feet. Unless otherwise approved by the applicable building code, storage of fine magnesium scrap in quantities greater than 50 cubic feet (1.4 m3) [six 55-gallon (208 L) steel drums] shall be maintained separated from other occupancies by an open space of at least 50 feet (15 240 mm) or by a fire-resistance rated barrier constructed and approved in accordance with applicable building code. 5906.4.3 Storage of greater than 1,000 cubic feet. Storage of fine magnesium scrap in quantities greater than 1,000 cubic feet (28 m3) shall be maintainted separated from all buildings other than those used for magnesium scrap recovery operations by a distance of not less than 100 feet (30 480 mm) unless otherwise approved by the applicable building code.
5906.5 Use of magnesium. The use of magnesium shall comply with Sections 5906.5.1 through 5906.5.8. 5906.5.1 Melting pots. Floors under and around melting pots shall be of noncombustible construction. 5906.5.2 Heat-treating ovens. Approved means shall be provided for control of magnesium fires in heat-treating ovens. 5906.5.3 Dust collection. Magnesium grinding, buffing and wire-brushing operations, other than rough finishing of castings, shall be provided with approved hoods or enclosures for dust collection which are connected to a liquid-precipitation type of separator that converts dust to sludge without contact (in a dry state) with any high-speed moving parts. 5906.5.3.1 Duct construction. Connecting ducts or suction tubes shall be completely grounded, as short as possible, and without bends. Ducts shall be fabricated and assembled with a smooth interior, with internal lap joints pointing in the direction of airflow and without unused capped side outlets, pockets or other dead-end spaces which allow an accumulation of dust. 5906.5.3.2 Independent dust separators. Each machine shall be equipped with an individual dust-separating unit. Exceptions: 1.One separator is allowed to serve two dust-producing units on multiunit machines. 2.One separator is allowed to serve not more than four portable dust-producing units in a single enclosure or stand. 5906.5.4 Power supply interlock. Power supply to machines shall be interlocked with exhaust airflow, and liquid pressure level or flow. The interlock shall be designed to shut down the machine it serves when the dust removal or separator system is not operating properly. | (N)5906.5 Use of magnesium. (Section deleted) (N)5906.5.1 Melting pots. (Section deleted) (N)5906.5.2 Heat-treating ovens. (Section deleted) (N)5906.5.3 Dust collection. (Section deleted) (N)5906.5.3.1 Duct construction. (Section deleted) (N)5906.5.3.2 Independent dust separators. (Section deleted) (N)5906.5.4 Power supply interlock. (Section deleted) |  | Use is regulated by the Building Code (F1 or F2) however the use of magnesium is not necessarily regulated by the building code. Consider deleting secthion 5906.5.3.2 | 5906.5 Use of magnesium. The use of magnesium shall comply with Sections 5906.5.1 through 5906.5.8 and only be conduted in buildings or structures that remain in accordance with the applicable building code. 5906.5.1 Melting pots. Floors under and around melting pots shall be of noncombustible construction. 5906.5.2 Heat-treating ovens. Approved means shall be provided for control of magnesium fires in heat-treating ovens. 5906.5.3 Dust collection. Where provided, magnesium grinding, buffing and wire-brushing operations, other than rough finishing of castings, shall be conduted with approved hoods or enclosures for dust collection in accordance with the applicable building code. 5906.5.3.1 Duct construction. Where provided, connecting ducts or suction tubes shall be maintained as completely grounded, as short as possible, and without bends. Ducts shall be maintined with a smooth interior, with internal lap joints pointing in the direction of airflow and without unused capped side outlets, pockets or other dead-end spaces which allow an accumulation of dust. 5906.5.3.2 Independent dust separators. Each machine shall be equipped with an individual dust-separating unit in accordance with the applicable building code. Exceptions: 1.One separator is allowed to serve two dust-producing units on multiunit machines. 2.One separator is allowed to serve not more than four portable dust-producing units in a single enclosure or stand. 5906.5.4 Power supply interlock. Where provided, power supply to machines shall be maintained to be interlocked with exhaust airflow, and liquid pressure level or flow. The interlock shall be maintained to shut down the machine it serves when the dust removal or separator system is not operating properly.
5906.5.5 Electrical equipment. Electric wiring, fixtures and equipment in the immediate vicinity of and attached to dust-producing machines, including those used in connection with separator equipment, shall be of approved types and shall be approved for use in Class II, Division 1 hazardous locations in accordance with NFPA 70. | (N)5906.5.5 Electrical equipment. Electric wiring, fixtures and equipment in the immediate vicinity of and attached to dustproducing machines, shall be maintained in accordance with the applicable building code. |  |  | (N)5906.5.5 Electrical equipment. Electric wiring, fixtures and equipment in the immediate vicinity of and attached to dustproducing machines, shall be maintained in accordance with Chapter 6 and remain in accordance with the applicable building code.
5906.5.6 Grounding. Equipment shall be securely grounded by permanent ground wires in accordance with NFPA 70. | (N)5906.5.6 Grounding. (Section deleted) |  |  | 5906.5.6 Grounding. Where required by the applicable building code, equipment shall be maintained securely grounded by permanent ground wires in accordance with NFPA 70.

## Ch60 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
6001.1 Scope. The storage and use of highly toxic and toxic materials shall comply with this chapter. Compressed gases shall also comply with Chapter 53. Exceptions: 1.Display and storage in Group M and storage in Group S occupancies complying with Section 5003.11. 2.Conditions involving pesticides or agricultural products as follows: 2.1.Application and release of pesticide, agricultural products and materials intended for use in weed abatement, erosion control, soil amendment or similar applications when applied in accordance with the manufacturer’s instruction and label directions. 2.2.Transportation of pesticides in compliance with the Federal Hazardous Materials Transportation Act and regulations thereunder. 2.3.Storage in dwellings or private garages of pesticides registered by the U.S. Environmental Protection Agency to be utilized in and around the home, garden, pool, spa and patio. 6001.2 Permits. Permits shall be required as set forth in Section 107.2. | 6001.1 Scope. The outside storage and use of highly toxic and toxic materials and the maintenance and operational aspects of inside storage and use of highly toxic and toxic materials shall comply with this chapter. Compressed gases shall also comply with Chapter 53. Exceptions: 1. Display and storage in Group M and storage in Group S occupancies complying with Section 5003.11. 2. Conditions involving pesticides or agricultural products as follows: 2.1. Application and release of pesticide, agricultural products and materials intended for use in weed abatement, erosion control, soil amendment or similar applications when applied in accordance with the manufacturer's instruction and label directions. 2.2. Transportation of pesticides in compliance with the Federal Hazardous Materials Transportation Act and regulations thereunder. 2.3. Storage in dwellings or private garages of pesticides registered by the U.S. Environmental Protection Agency to be utilized in and around the home, garden, pool, spa and patio. 6001.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | No change
6003.1.4 Indoor storage. Indoor storage of highly toxic and toxic solids and liquids shall comply with Sections 6003.1.4.1 and 6003.1.4.2. | 6003.1.4 Indoor storage. Indoor storage of highly toxic and toxic solids and liquids shall comply with the applicable building code. |  |  | No change
6003.1.4.1 Floors. In addition to the requirements set forth in Section 5004.12, floors of storage areas shall be of liquid-tight construction. 6003.1.4.2 Separation—highly toxic solids and liquids. In addition to the requirements set forth in Section 5003.9.8, highly toxic solids and liquids in storage shall be located in approved hazardous material storage cabinets or isolated from other hazardous material storage by construction in accordance with the International Building Code. | (N)6003.1.4.1 Floors. (Section deleted) (N)6003.1.4.2 Separation—highly toxic solids and liquids. (Section deleted) |  | regulate the storage location? | No change
6003.2.5 Weather protection for highly toxic liquids and solids—outdoor storage or use. Where overhead weather protection is provided for outdoor storage or use of highly toxic liquids or solids, and the weather protection is attached to a building, the storage or use area shall either be equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1, or storage or use vessels shall be fire resistive. Weather protection shall be provided in accordance with Section 5004.13 for storage and Section 5005.3.9 for use. | (N)6003.2.5 Weather protection for highly toxic liquids and solids—outdoor storage or use. (Section deleted) |  |  | No change
6004.1.2 Gas cabinets. Gas cabinets containing highly toxic or toxic compressed gases shall comply with Section 5003.8.6 and the following requirements: 1.The average ventilation velocity at the face of gas cabinet access ports or windows shall not be less than 200 feet per minute (1.02 m/s) with a minimum of 150 feet per minute (0.76 m/s) at any point of the access port or window. 2.Gas cabinets shall be connected to an exhaust system. 3.Gas cabinets shall not be used as the sole means of exhaust for any room or area. 4.The maximum number of cylinders located in a single gas cabinet shall not exceed three, except that cabinets containing cylinders not exceeding 1 pound (0.454 kg) net contents are allowed to contain up to 100 cylinders. 5.Gas cabinets required by Section 6004.2 or 6004.3 shall be equipped with an approved automatic sprinkler system in accordance with Section 903.3.1.1. Alternative fire-extinguishing systems shall not be used. | 6004.1.2 Gas cabinets. Gas cabinets containing highly toxic or toxic compressed gases shall comply with Section 5003.8.6 and the following requirements: 1. The average ventilation velocity at the face of gas cabinet access ports or windows shall be not less than 200 feet per minute (1.02 m/s) with not less than 150 feet per minute (0.76 m/s) at any point of the access port or window. 2. Gas cabinets shall be connected to an exhaust system. 3. Gas cabinets shall not be used as the sole means of exhaust for any room or area. 4. The maximum number of cylinders located in a single gas cabinet shall not exceed three, except that cabinets containing cylinders not exceeding 1 pound (0.454 kg) net contents are allowed to contain up to 100 cylinders.5. Gas cabinets required by Section 6004.2 or 6004.3 shall be equipped with an approved automatic sprinkler system in accordance with the applicable building code. Alternative fire-extinguishing systems shall not be used. |  |  | No change
6004.1.3 Exhausted enclosures. Exhausted enclosures containing highly toxic or toxic compressed gases shall comply with Section 5003.8.5 and the following requirements: 1.The average ventilation velocity at the face of the enclosure shall not be less than 200 feet per minute (1.02 m/s) with a minimum of 150 feet per minute (0.76 m/s). 2.Exhausted enclosures shall be connected to an exhaust system. 3.Exhausted enclosures shall not be used as the sole means of exhaust for any room or area. 4.Exhausted enclosures required by Section 6004.2 or 6004.3 shall be equipped with an approved automatic sprinkler system in accordance with Section 903.3.1.1. Alternative fire-extinguishing systems shall not be used. | 6004.1.3 Exhausted enclosures. Exhausted enclosures containing highly toxic or toxic compressed gases shall comply with Section 5003.8.5 and the following requirements: 1. The average ventilation velocity at the face of the enclosure shall be not less than 200 feet per minute (1.02 m/s) with not less than 150 feet per minute (0.76 m/s). 2. Exhausted enclosures shall be connected to an exhaust system. 3. Exhausted enclosures shall not be used as the sole means of exhaust for any room or area. 4. Exhausted enclosures required by Section 6004.2 or 6004.3 shall be equipped with an approved automatic sprinkler system in accordance with the applicable building code. Alternative fireextinguishing systems shall not be used. |  |  | No change
6004.3.3 Outdoor storage weather protection for portable tanks and cylinders. Weather protection in accordance with Section 5004.13 shall be provided for portable tanks and cylinders located outdoors and not within gas cabinets or exhausted enclosures. The storage area shall be equipped with an approved automatic sprinkler system in accordance with Section 903.3.1.1. Exception: An automatic sprinkler system is not required when: 1.All materials under the weather protection structure, including hazardous materials and the containers in which they are stored, are non-combustible. 2.The weather protection structure is located not less than 30 feet (9144 mm) from combustible materials or structures or is separated from such materials or structures using a fire barrier complying with Section 6004.3.2.1.1. | 6004.3.3 Outdoor storage weather protection for portable tanks and cylinders. Weather protection in accordance with Section 5004.13 shall be provided for portable tanks and cylinders located outdoors and not within gas cabinets or exhausted enclosures. The storage area shall be equipped with an approved automatic sprinkler system in accordance with the applicable building code. Exception: An automatic sprinkler system is not required when: 1. All materials under the weather protection structure, including hazardous materials and the containers in which they are stored, are noncombustible. 2. The weather protection structure is located not less than 30 feet (9144 mm) from combustible materials or structures or is separated from such materials or structures using a fire barrier complying with Section 6004.3.2.1.1. |  |  | No change
6004.2.2.5 Piping and controls—stationary tanks. In addition to the requirements of Section 5003.2.2, piping and controls on stationary tanks shall comply with the following requirements: 1.Pressure relief devices shall be vented to a treatment system designed in accordance with Section 6004.2.2.7. Exception: Pressure relief devices on outdoor tanks provided exclusively for relieving pressure due to fire exposure are not required to be vented to a treatment system provided that: 1.The material in the tank is not flam-mable. 2.The tank is not located in a diked area with other tanks containing combustible materials. 3.The tank is located not less than 30 feet (9144 mm) from combustible materials or structures or is shielded by a fire barrier complying with Section 6004.3.2.1.1. 2.Filling or dispensing connections shall be provided with a means of local exhaust. Such exhaust shall be designed to capture fumes and vapors. The exhaust shall be directed to a treatment system in accordance with Section 6004.2.2.7. 3.Stationary tanks shall be provided with a means of excess flow control on all tank inlet or outlet connections. Exceptions: 1.Inlet connections designed to prevent backflow. 2.Pressure relief devices. | (N)6004.2.2.5 Piping and controls - stationary tanks. In addition to the requirements of Section 5003.2.2, piping and controls on stationary tanks shall comply with the following requirements: 1. Pressure relief devices shall be vented to a treatment system designed in accordance with Section 6004.2.2.7. Exception: Pressure relief devices on outdoor tanks provided exclusively for relieving pressure due to fire exposure are not required to be vented to a treatment system provided that: 1. The material in the tank is not flammable. 2. The tank is located not less than 30 feet (9144 mm) from combustible materials or structures or is shielded by a fire barrier complying with Section 6004.3.2.1.1. 2. Filling or dispensing connections shall be provided with a means of local exhaust. Such exhaust shall be designed to capture fumes and vapors. The exhaust shall be directed to a treatment system in accordance with Section 6004.2.2.7. 3. Stationary tanks shall be provided with a means of excess flow control on all tank inlet or outlet connections. Exceptions: 1. Inlet connections designed to prevent backflow. 2. Pressure relief devices. |  |  | No change
6004.2.2.6 Gas rooms. Gas rooms shall comply with Section 5003.8.4 and both of the following requirements: 1.The exhaust ventilation from gas rooms shall be directed to an exhaust system. 2.Gas rooms shall be equipped with an approved automatic sprinkler system. Alternative fire-extinguishing systems shall not be used. | (N)6004.2.2.6 Gas rooms. Gas rooms shall comply with Section 5003.8.4 and the following requirement: 1. The exhaust ventilation from gas rooms shall be directed to an exhaust system. |  | Why is item 2 removed? | Add item 2 similar to above sections?
6004.2.2.8 Emergency power. Emergency power in accordance with the Section 604 and NFPA 70 shall be provided in lieu of standby power where any of the following systems are required: 1.Exhaust ventilation system. 2.Treatment system. 3.Gas detection system. 4.Smoke detection system. 5.Temperature control system. 6.Fire alarm system. 7.Emergency alarm system. Exception: Emergency power is not required for mechanical exhaust ventilation, treatment systems and temperature control systems where approved fail-safe engineered systems are installed. | (N)6004.2.2.8 Emergency power. Emergency power shall be maintained in accordance with the applicable building code. |  |  | (N)6004.2.2.8 Emergency power. Emergency power shall be maintained in accordance with Chapter 6 and remain in accordance with the applicable building code.
None | (N)6004.2.2.8.1 Fail-safe engineered systems. (Section deleted) |  |  | No change
6004.2.2.9 Automatic fire detection system—highly toxic compressed gases. An approved automatic fire detection system shall be installed in rooms or areas where highly toxic compressed gases are stored or used. Activation of the detection system shall sound a local alarm. The fire detection system shall comply with Section 907. | (N)6004.2.2.9 Automatic fire detection system—highly toxic compressed gases. (Section deleted) |  | Delete sentence two and combine with sentence 3 | 6004.2.2.9 Automatic fire detection system—highly toxic compressed gases. Where provided, an approved automatic fire detection system shall be maintained in rooms or areas where highly toxic compressed gases are stored or used. Activation of the detection system shall sound a local alarm. The fire detection system shall comply with Chapter 9 and remain in accordance with the applicable building code.

## Ch61 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
6101.2 Permits. Permits shall be required as set forth in Section 107.2. Distributors shall not fill an LP-gas container for which a permit is required unless a permit for installation has been issued for that location by the fire code official, except when the container is for temporary use on construction sites. | 6101.2 Permits. Permits shall be required as set forth in Section 107.2. Distributors shall not fill an LP-gas container for which a permit is required unless a permit for installation has been issued for that location by the fire code official, except when the container is for temporary use on construction sites. |  |  | No change
6103.1 General. LP-gas equipment shall be installed in accordance with the International Fuel Gas Code and NFPA 58, except as otherwise provided in this chapter. | (N)6103.1 General. LP-gas equipment shall be maintained in accordance with the code under which it was installed |  | How are portable devices regulated? | 6103.1 General. Portable LP-gas equipment shall be installed in accordance with the International Fuel Gas Code and NFPA 58, except as otherwise provided in this chapter.
6103.3 Location of equipment and piping. Equipment and piping shall not be installed in locations where such equipment and piping is prohibited by the International Fuel Gas Code. | (N)6103.3 Location of equipment and piping. (Section deleted) |  |  | No change
6104.1 General. The storage and handling of LP-gas and the installation and maintenance of related equipment shall comply with NFPA 58 and be subject to the approval of the fire code official, except as provided in this chapter. | (N)6104.1 General. The storage and handling of LP-gas and the maintenance of related equipment shall comply with applicable building code. |  | How are portable devices regulated? | 6104.1 General. The storage and handling of Portable LP-gas and the installation and maintenance of related equipment shall comply with NFPA 58 and be subject to the approval of the fire code official, except as provided in this chapter.
6104.2 Maximum capacity within established limits. Within the limits established by law restricting the storage of liquefied petroleum gas for the protection of heavily populated or congested areas, the aggregate capacity of any one installation shall not exceed a water capacity of 2,000 gallons (7570 L) (see Section 3 of the Sample Legislation for Adoption of the International Fire Code on page xxi). Exception: In particular installations, this capacity limit shall be determined by the fire code official, after consideration of special features such as topographical conditions, nature of occupancy, and proximity to buildings, capacity of proposed LP-gas containers, degree of fire protection to be provided and capabilities of the local fire department. 6104.3 Container location. LP-gas containers shall be located with respect to buildings, public ways and lot lines of adjoining property that can be built upon, in accordance with Table 6104.3. 6104.3.1 Installation on roof prohibited. LP-gas containers used in stationary installations shall not be located on the roofs of buildings. 6104.3.2 Special hazards. LP-gas containers shall also be located with respect to special hazards including, but not limited to, above-ground flammable or combustible liquid tanks, oxygen or gaseous hydrogen containers, flooding or electric power lines as specified in Section 6.4.5 of NFPA 58. 6104.4 Multiple LP-gas container installations. Multiple LP-gas container installations with a total water storage capacity of more than 180,000 gallons (681 300 L) [150,000-gallon (567 750 L) LP-gas capacity] shall be subdivided into groups containing not more than 180,000 gallons (681 300 L) in each group. Such groups shall be separated by a distance of not less than 50 feet (15 240 mm), unless the containers are protected in accordance with one of the following: 1.Mounded in an approved manner. 2.Protected with approved insulation on areas that are subject to impingement of ignited gas from pipelines or other leakage. 3.Protected by firewalls of approved construction. 4.Protected by an approved system for application of water as specified in Table 6.4.2 of NFPA 58. 5.Protected by other approved means. Where one of these forms of protection is provided, the separation shall not be less than 25 feet (7620 mm) between LP-gas container groups. | (N)6104.2 Maximum capacity within established limits. (Section deleted) (N)6104.3 Container location. (Section deleted) (N)6104.3.1 Installation on roof prohibited. (Section deleted) (N)6104.3.2 Special hazards. (Section deleted) (N)6104.4 Multiple LP-gas container installations. (Section deleted) |  |  | No change
TABLE 6104.3 LOCATION OF LP-GAS CONTAINERS | (N)TABLE 6104.3 LOCATION OF LP-GAS CONTAINERS (Table deleted) |  |  | No change
6106.4 DOTn cylinders filled on site. DOTn cylinders in stationary service that are filled on site and therefore are not under the jurisdiction of DOTn either shall be requalified in accordance with DOTn requirements or shall be visually inspected within 12 years of the date of manufacture or within 5 years from May 1, 2008, whichever is later, and within every 5 years thereafter, in accordance with the following: 1.Any cylinder that fails one or more of the criteria in Item 3 shall not be refilled or continued in service until the condition is corrected. 2.Personnel shall be trained and qualified to perform inspections. 3.Visual inspection shall be performed in accordance with the following: 3.1.The cylinder is checked for exposure to fire, dents, cuts, digs, gouges, and corrosion according to CGA C-6, Standards for Visual Inspection of Steel Compressed Gas Cylinders, except that paragraph 4.2.1(1) of that standard (which requires tare weight certification), shall not be part of the required inspection criteria. 3.2.The cylinder protective collar (where utilized) and the foot ring are intact and are firmly attached. 3.3.The cylinder is painted or coated to retard corrosion. 3.4.The cylinder pressure relief valve indicates no visible damage, corrosion of operating components, or obstructions. 3.5.There is no leakage from the cylinder or its appurtenances that is detectable without the use of instruments. 3.6.The cylinder is installed on a firm foundation and is not in contact with the soil. 3.7.A cylinder that passed the visual inspection shall be marked with the month and year of the examination followed by the letter “E” (example: 10-01E, indicating requalification in October 2001 by the external inspection method). 3.8.The results of the visual inspection shall be documented, and a record of the inspection shall be retained for a 5-year period. Exception: Any inspection procedure outlined in Items 3.1 through 3.8 that would require a cylinder to be moved in such a manner that disconnection from the piping system would be necessary shall be omitted, provided the other inspection results do not indicate further inspection is warranted. | 6106.4 DOTn cylinders filled on site. U.S. Department of Transportation (DOTn) cylinders in stationary service that are filled on site and therefore are not under the jurisdiction of DOTn either shall be requalified in accordance with DOTn requirements or shall be visually inspected within 12 years of the date of manufacture or within five years from May 1, 2008, whichever is later, and within every five years thereafter, in accordance with the following: 1. Any cylinder that fails one or more of the criteria in Item 3 shall not be refilled or continued in service until the condition is corrected. 2. Personnel shall be trained and qualified to perform inspections. 3. Visual inspection shall be performed in accordance with the following: 3.1. The cylinder is checked for exposure to fire, dents, cuts, digs, gouges, and corrosion according to CGA C-6, Standards for Visual Inspection of Steel Compressed Gas Cylinders, except that paragraph 4.2.1(1) of that standard (which requires tare weight certification), shall not be part of the required inspection criteria. 3.2. The cylinder protective collar (where utilized) and the foot ring are intact and are firmly attached. 3.3. The cylinder is painted or coated to retard corrosion. 3.4. The cylinder pressure relief valve indicates no visible damage, corrosion of operating components, or obstructions. 3.5. There is no leakage from the cylinder or its appurtenances that is detectable without the use of instruments. 3.6. The cylinder is installed on a firm foundation and is not in contact with the soil. 3.7. A cylinder that passed the visual inspection shall be marked with the month and year of the examination followed by the letter "E" (example: 10-01E, indicating requalification in October 2001 by the external inspection method). 3.8. The results of the visual inspection shall be documented, and a record of the inspection shall be retained for a five-year period. Exception: Any inspection procedure outlined in Items 3.1 through 3.8 that would require a cylinder be moved in such a manner that disconnection from the piping system would be necessary shall be omitted, provided the other inspection results do not indicate further inspection is warranted. |  |  | no change
6108.1 General. Fire protection shall be provided for installations having LP-gas storage containers with a water capacity of more than 4,000 gallons (15 140 L), as required by Section 6.25 of NFPA 58. | (N)6108.1 General. Fire protection for installations having LP-gas storage containers shall be maintained in accordance with the applicable building code. |  | The 2015 amendment affects all fire protection systems. This is a construction related item. | no change
6109.11.2 Construction. The construction of such buildings and rooms shall comply with requirements for Group H occupancies in the International Building Code, Chapter 10 of NFPA 58 and both of the following: 1.Adequate vents shall be provided to the outside at both top and bottom, located at least 5 feet (1524 mm) from building openings. 2.The entire area shall be classified for the purposes of ignition source control in accordance with Section 6.22 of NFPA 58. | (N)6109.11.2 Construction (Section deleted) |  | Should reference be to the USBC? Ignition source control is an operational concern not a construction concern. | 6109.11.2 Operations and Maintenance. Buildings and rooms used for the storage rooms shall be maintained in accordance with the applicable building code, Chapter 10 of NFPA 58 and both of the following: 1. Required vents to the outside at both top and bottom, shall be maintained in an operable condition. 2.The entire area shall be classified for the purposes of ignition source control in accordance with Section 6.22 of NFPA 58.
6111.2 Unattended parking. The unattended parking of LP-gas tank vehicles shall be in accordance with Sections 6111.2.1 and 6111.2.2. Exception: The unattended outdoor parking of LP-gas tank vehicles may also be in accordance with Section 9.7.2 of NFPA 58. 6111.2.1 Near residential, educational and institutional occupancies and other high-risk areas. LP-gas tank vehicles shall not be left unattended at any time on residential streets or within 500 feet (152 m) of a residential area, apartment or hotel complex, educational facility, hospital or care facility. Tank vehicles shall not be left unattended at any other place that would, in the opinion of the fire code official, pose an extreme life hazard. 6111.2.2 Durations exceeding 1 hour. LP-gas tank vehicles parked at any one point for longer than 1 hour shall be located as follows: 1.Off public streets, highways, public avenues or public alleys. 2.Inside of a bulk plant. 3.At other approved locations not less than 50 feet (15 240 mm) from buildings other than those approved for the storage or servicing of such vehicles. | 6111.2 Unattended parking. The unattended parking of LP-gas tank vehicles shall be in accordance with Sections 6111.2.1 and 6111.2.2. Exception: The unattended outdoor parking of LP-gas tank vehicles may also be in accordance with Section 9.7.2 of NFPA 58. |  | Sections 6111.2.1 and 6111.2.2 from 2012 are identical to that in the 2015 IFC | no change

## Ch62 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
6201.2 Permits. Permits shall be required for organic peroxides as set forth in Section 107.2. | 6201.2 Permits. Permits shall be required for organic peroxides as set forth in Section 107.2. |  |  | No change
6203.1 Quantities not exceeding the maximum allowable quantity per control area. The storage and use of organic peroxides in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with Sections 5001, 5003, 6201 and 6203. | (N)6203.1 Storage and use. The storage and use of organic peroxides in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be maintained in accordance with the applicable building code. |  |  | 6203.1 Quantities not exceeding the maximum allowable quantity per control area. The storage and use of organic peroxides in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be maintained in accordance with Sections 5001, 5003, 6201 and 6203.
6203.1.1 Special limitations for indoor storage and use by occupancy. The indoor storage and use of organic peroxides shall be in accordance with Sections 6203.1.1.1 through 6203.1.1.4. | (N)6203.1.1 Special limitations for indoor storage and use by occupancy. The indoor storage and use of organic peroxides shall be maintained in accordance with the applicable building code. |  |  | 6203.1.1 Special limitations for indoor storage and use by occupancy. The indoor storage and use of organic peroxides shall be maintained in accordance with Sections 6203.1.1.1 through 6203.1.1.4.
6203.1.1.1 Group A, E, I or U occupancies. In Group A, E, I or U occupancies, any amount of unclassified detonable and Class I organic peroxides shall be stored in accordance with the following: 1.Unclassified detonable and Class I organic peroxides shall be stored in hazardous materials storage cabinets complying with Section 5003.8.7. 2.The hazardous materials storage cabinets shall not contain other storage. | (N)6203.1.1.1 Group A, E, I or U occupancies. (Section deleted) |  |  | 6203.1.1.1 Group A, E, I or U occupancies. Unless otherwise approved by the applicable building code, in Group A, E, I or U occupancies, any amount of unclassified detonable and Class I organic peroxides shall be stored in accordance with the following: 1.Unclassified detonable and Class I organic peroxides shall be stored in hazardous materials storage cabinets complying with Section 5003.8.7. 2.The hazardous materials storage cabinets shall not contain other storage.
6203.1.1.3 Group B, F, M or S occupancies. Unclassified detonable and Class I organic peroxides shall not be stored or used in offices, or retail sales areas of Group B, F, M or S occupancies. | (N)6203.1.1.3 Group B, F, M or S occupancies. (Section deleted) |  |  | 6203.1.1.3 Group B, F, M or S occupancies. Unless otherwise approved by the applicable building code, unclassified detonable and Class I organic peroxides shall not be stored or used in offices, or retail sales areas of Group B, F, M or S occupancies.
6203.1.1.4 Classrooms. In classrooms in Group B, F or M occupancies, any amount of unclassified detonable and Class 1 organic peroxides shall be stored in accordance with the following. 1.Unclassified detonable and Class 1 organic peroxides shall be stored in hazardous materials storage cabinets complying with Section 5003.8.7. 2.The hazardous materials storage cabinets shall not contain other storage. | (N)6203.1.1.4 Classrooms. In classrooms in Group B, F or M occupancies, any amount of unclassified detonable and Class 1 organic peroxides shall be stored in accordance with the applicable building code. |  |  | 6203.1.1.4 Classrooms. Unless otherwise approved by the applicable building code, in classrooms in Group B, F or M occupancies, any amount of unclassified detonable and Class 1 organic peroxides shall be stored in accordance with the following. 1.Unclassified detonable and Class 1 organic peroxides shall be stored in hazardous materials storage cabinets complying with Section 5003.8.7. 2.The hazardous materials storage cabinets shall not contain other storage.
6203.2 Quantities exceeding the maximum allowable quantity per control area. The storage and use of organic peroxides in amounts exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with Chapter 50 and this chapter. | (N)6203.2 Quantities exceeding the maximum allowable quantity per control area. (Section deleted) |  |  | 6203.2 Quantities exceeding the maximum allowable quantity per control area. The storage and use of organic peroxides in amounts exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be maintained in accordance with Chapter 50, this chapter and comply with the applicable building code.
6204.1.1 Detached storage. Storage of organic peroxides shall be in detached buildings when required by Section 5003.8.2. | (N)6204.1.1 Detached storage. (Section deleted) |  |  | 6204.1.1 Detached storage. Unless otherwise approved by the applicable building code, storage of organic peroxides shall be in detached buildings when required by Section 5003.8.2.
TABLE 6204.1.2 ORGANIC PEROXIDES—DISTANCE TO EXPOSURES FROM DETACHED STORAGE BUILDINGS OR OUTDOOR STORAGE AREAS | (N)TABLE 6204.1.2 ORGANIC PEROXIDES—DISTANCE TO EXPOSURES FROM DETACHED STORAGE BUILDINGS OR OUTDOOR STORAGE AREAS (Table deleted) |  |  | TABLE 6204.1.2 ORGANIC PEROXIDES—DISTANCE TO EXPOSURES FROM DETACHED STORAGE BUILDINGS OR OUTDOOR STORAGE AREAS
6204.1.2 Distance from detached buildings to exposures. In addition to the requirements of the International Building Code, detached storage buildings for Class I, II, III, IV and V organic peroxides shall be located in accordance with Table 6204.1.2. Detached buildings containing quantities of unclassified detonable organic peroxides in excess of those set forth in Table 5003.8.2 shall be located in accordance with Table 5604.5.2(1). 6204.1.3 Liquid-tight floor. In addition to the requirements of Section 5004.12, floors of storage areas shall be of liquid-tight construction. 6204.1.4 Electrical wiring and equipment. In addition to the requirements of Section 5003.9.4, electrical wiring and equipment in storage areas for Class I or II organic peroxides shall comply with the requirements for electrical Class I, Division 2 locations. 6204.1.5 Smoke detection. An approved supervised smoke detection system in accordance with Section 907 shall be provided in rooms or areas where Class I, II or III organic peroxides are stored. Activation of the smoke detection system shall sound a local alarm. Exception: A smoke detection system shall not be required in detached storage buildings equipped throughout with an approved automatic fire-extinguishing system complying with Chapter 9. 6204.1.6 Maximum quantities. Maximum allowable quantities per building in a mixed occupancy building shall not exceed the amounts set forth in Table 5003.8.2. Maximum allowable quantities per building in a detached storage building shall not exceed the amounts specified in Table 6204.1.2. | (N)6204.1.2 Distance from detached buildings to exposures. Detached storage buildings for Classes I, II, III, IV and V organic peroxides shall be located in accordance with the applicable building code. Detached buildings containing quantities of unclassified detonable organic peroxides shall be located in accordance with the applicable building code. (N)6204.1.3 Liquid-tight floor. Liquid-tight floors shall be maintained in accordance with the applicable building code. (N)6204.1.4 Electrical wiring and equipment. Electrical wiring and equipment in storage areas for Class I or II organic peroxides shall be maintained in accordance with the applicable building code. (N)6204.1.5 Smoke detection. Smoke detection systems shall be maintained in accordance with the applicable building code. (N)6204.1.6 Maximum quantities. Maximum allowable quantities per building in a mixed occupancy building shall not exceed the amounts set forth by the applicable building code. Maximum allowable quantities per building in a detached storage building shall not exceed the amounts set forth by the applicable building code. |  |  | 6204.1.2 Distance from detached buildings to exposures. Detached storage buildings for Classes I, II, III, IV and V organic peroxides shall be located in accordance with the applicable building code and maintain separation distances from exposures in accordance with Table 6304.1.2. Detached buildings containing quantities of unclassified detonable organic peroxides in excess of those set forth in Table 5003.8.2, shall be located in accordance with the applicable building code and maintain separation distances from exposures in accordance with Table 5604.5.2(1). 6204.1.3 Liquid-tight floor. Where provided, liquid-tight floors shall be maintained and remain in accordance with the applicable building code. 6204.1.4 Electrical wiring and equipment. Electrical wiring and equipment in storage areas for Class I or II organic peroxides shall be maintained in accordance with Chapter 6 and remain as classified in accordance with the applicable building code. 6204.1.5 Smoke detection. Smoke detection systems shall be maintained in accordance with Chapter 9 and remain in accordance with the applicable building code. 6204.1.6 Maximum quantities. Maximum allowable quantities per building in a mixed occupancy building shall not exceed the amounts set forth by Table 5003.8.2 unless approved by the applicable building code. Maximum allowable quantities per building in a detached storage building shall not exceed the amounts set forth by Table 6204.1.2 and teh applicable building code.
6204.1.10 Explosion control. Indoor storage rooms, areas and buildings containing unclassified detonable and Class I organic peroxides shall be provided with explosion control in accordance with Section 911. 6204.1.11 Standby power. Standby power in accordance with Section 604 shall be provided for storage areas of Class I and unclassified detonable organic peroxide. | (N)6204.1.10 Explosion control. Indoor storage rooms, areas and buildings containing explosion control shall be maintained in accordance with the applicable building code. (N)6204.1.11 Standby power. Standby power shall be maintained in accordance with the applicable building code. |  |  | 6204.1.10 Explosion control. Indoor storage rooms, areas and buildings containing unclassified detonable and Class 1 organic peroxides shall maintain explosion control in accordance with Chapter 9 and remain in accordance with the applicable building code. 6204.1.11 Standby power. Standby power shall be maintained in accordance with Section 604 for storage areas of Class 1 and unclassified detonable organic peroxide and remain in accordance with the applicable building code.
None | (N)6204.1.11.1 Fail-safe engineered systems. (Section deleted) |  |  | No change
6204.2.5 Separation. In addition to the requirements of Section 5003.9.8, outdoor storage areas for organic peroxides in amounts exceeding those specified in Table 5003.8.2 shall be located a minimum distance of 50 feet (15 240 mm) from other hazardous material storage. | 6204.2.5 Separation. In addition to the requirements of Section 5003.9.8, outdoor storage areas for organic peroxides in amounts exceeding those specified by the applicable building code shall be located a minimum distance of 50 feet (15 240 mm) from other hazardous material storage. |  |  | 6204.2.5 Separation. In addition to the requirements of Section 5003.9.8, outdoor storage areas for organic peroxides in amounts exceeding those specified in Table 5003.8.2 shall be located a minimum distance of 50 feet (15 240 mm) from other hazardous material storage.
6204.2.3 Maximum quantities. Maximum quantities of organic peroxides in outdoor storage shall be in accordance with Table 6204.1.2. | (N)6204.2.3 Maximum quantities. Maximum quantities of organic peroxides in outdoor storage shall be in accordance with the applicable building code. |  |  | 6204.2.3 Maximum quantities. Maximum quantities of organic peroxides in outdoor storage shall be in accordance with Table 6204.1.2.

## Ch63 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
6301.2 Permits. Permits shall be required as set forth in Section 107.2. | 6301.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
6303.1 Quantities not exceeding the maximum allowable quantity per control area. The storage and use of oxidizing materials in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with Sections 5001, 5003, 6301 and 6303. Oxidizing gases shall also comply with Chapter 53. | (N)6303.1 Storage and use. The storage and use of oxidizing materials shall be maintained in accordance with the applicable building code. |  |  | 6303.1 Quantities not exceeding the maximum allowable quantity per control area. The storage and use of oxidizing materials in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be maintained in accordance with Sections 5001, 5003, 6301 and 6303. Oxidizing gases shall also comply with Chapter 53.
6303.1.1 Special limitations for indoor storage and use by occupancy. The indoor storage and use of oxidizing materials shall be in accordance with Sections 6303.1.1.1 through 6303.1.1.3. | (N)6303.1.1 Special limitations for indoor storage and use by occupancy. (Section deleted) |  |  | 6303.1.1 Special limitations for indoor storage and use by occupancy. The indoor storage and use of oxidizing materials shall be in accordance with Sections 6303.1.1.1 through 6303.1.1.3.
6303.1.1.1 Class 4 liquid and solid oxidizers. The storage and use of Class 4 liquid and solid oxidizers shall comply with Sections 6303.1.1.1.1 through 6303.1.1.1.4. | (N)6303.1.1.1 Class 4 liquid and solid oxidizers. (Section deleted) |  |  | 6303.1.1.1 Class 4 liquid and solid oxidizers. The storage and use of Class 4 liquid and solid oxidizers shall comply with Sections 6303.1.1.1.1 through 6303.1.1.1.4.
6303.1.1.1.1 Group A, E, I or U occupancies. In Group A, E, I or U occupancies, any amount of Class 4 liquid and solid oxidizers shall be stored in accordance with the following: 1.Class 4 liquid and solid oxidizers shall be stored in hazardous materials storage cabinets complying with Section 5003.8.7. 2.The hazardous materials storage cabinets shall not contain other storage. | 6303.1.1.1.1 Group A, E, I or U occupancies. In Group A, E, I or U occupancies, any amount of Class 4 liquid and solid oxidizers shall be stored in accordance with the following: Class 4 liquid and solid oxidizers shall be stored in hazardous materials storage cabinets complying with Section 5003.8.7. |  |  | 6303.1.1.1.1 Group A, E, I or U occupancies. Unless otherwise approved by the applicable building code, in Group A, E, I or U occupancies, any amount of Class 4 liquid and solid oxidizers shall be stored in accordance with the following: 1.Class 4 liquid and solid oxidizers shall be stored in hazardous materials storage cabinets complying with Section 5003.8.7. 2.The hazardous materials storage cabinets shall not contain other storage.
6303.1.1.2 Class 3 liquid and solid oxidizers. A maximum of 200 pounds (91 kg) of solid or 20 gallons (76 L) of liquid Class 3 oxidizer is allowed in Group I occupancies when such materials are necessary for maintenance purposes or operation of equipment. The oxidizers shall be stored in approved containers and in an approved manner. | (N)6303.1.1.2 Class 3 liquid and solid oxidizers. (Section deleted) (N)6303.1.1.3 Oxidizing gases. (Section deleted) |  |  | 6303.1.1.2 Class 3 liquid and solid oxidizers. Unless otherwise approved by the applicable building code, a maximum of 200 pounds (91 kg) of solid or 20 gallons (76 L) of liquid Class 3 oxidizer is allowed in Group I occupancies when such materials are necessary for maintenance purposes or operation of equipment. The oxidizers shall be stored in approved containers and in an approved manner.
6303.1.2 Emergency shutoff. Compressed gas systems conveying oxidizing gases shall be provided with approved manual or automatic emergency shutoff valves that can be activated at each point of use and at each source. | (N)6303.1.2 Emergency shutoff. Shutoff valves shall be maintained in accordance with the applicable building code. |  |  | 6303.1.2 Emergency shutoff. Compressed gas systems conveying oxidizing gases shall maintain approved manual or automatic emergency shutoff valves that can be activated at each point of use and at each source in accordance with the applicable building code.
6303.1.2.1 Shutoff at source. A manual or automatic fail-safe emergency shutoff valve shall be installed on supply piping at the cylinder or bulk source. Manual or automatic cylinder valves are allowed to be used as the required emergency shutoff valve when the source of supply is limited to unmanifolded cylinder sources. | (N)6303.1.2.1 Shutoff at source. (Section deleted) (N)6303.1.2.2 Shutoff at point of use. (Section deleted) |  |  | no change
6303.1.3 Ignition source control. Ignition sources in areas containing oxidizing gases shall be controlled in accordance with Section 5003.7. | (N)6303.1.3 Ignition source control. Ignition sources in areas containing oxidizing gases shall be controlled in accordance with the applicable building code. |  |  | 6303.1.3 Ignition source control. Ignition sources in areas containing oxidizing gases shall be controlled in accordance with Section 5003.7
6303.2 Quantities exceeding the maximum allowable quantity per control area. The storage and use of oxidizing materials in amounts exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with Chapter 50 and this chapter. | (N)6303.2 Class 1 oxidizer storage configuration. The storage configuration of Class I liquid and solid oxidizers shall be as set forth in accordance with the applicable building code. |  |  | 6303.2 Class 1 oxidizer storage configuration. The storage configuration of Class I liquid and solid oxidizers shall be as set forth in table 6303.2
None | (N)TABLE 6303.2 STORAGE OF CLASS 1 OXIDIZER LIQUIDS AND SOLIDS (Table deleted) |  |  | Do not delete the table
6304.1 Indoor storage. Indoor storage of oxidizing materials in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1) shall be in accordance with Sections 5001, 5003 and 5004 and this chapter. 6304.1.1 Detached storage. Storage of liquid and solid oxidizers shall be in detached buildings when required by Section 5003.8.2. 6304.1.2 Distance from detached storage buildings to exposures. In addition to the requirements of the International Building Code, detached storage buildings shall be located in accordance with Table 6304.1.2. 6304.1.3 Explosion control. Indoor storage rooms, areas and buildings containing Class 4 liquid or solid oxidizers shall be provided with explosion control in accordance with Section 911. 6304.1.4 Automatic sprinkler system. The automatic sprinkler system shall be designed in accordance with NFPA 430. 6304.1.5 Liquid-tight floor. In addition to Section 5004.12, floors of storage areas for liquid and solid oxidizers shall be of liquid-tight construction. | (N)6304.1 Indoor storage. Indoor storage of oxidizing materials shall be maintained in accordance with the applicable building code. (N)6304.1.1 Explosion control. Explosion control for indoor storage rooms, areas and buildings containing Class 4 liquid or solid oxidizers shall be maintained in accordance with the applicable building code. (N)6304.1.2 Automatic sprinkler system. The automatic sprinkler system for oxidizer storage shall be maintained in accordance with the applicable building code. (N)6304.1.3 Liquid-tight floor. Liquidtight floors of storage areas for liquid and solid oxidizers shall be maintained in accordance with the applicable building code. (N)6304.1.4 Smoke detection. Smoke detection systems shall be maintained in accordance with the applicable building code. (N)6304.1.5 Storage conditions. The maximum quantity of oxidizers per building in storage buildings shall be maintained in accordance with the applicable building code. |  |  | 6304.1 Indoor storage. Indoor storage of oxidizing materials in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1) shall be maintained in accordance with Sections 5001, 5003 and 5004, this chapter and comply with the applicable building code. 6304.1.1 Explosion control. Explosion control for indoor storage rooms, areas and buildings containing Class 4 liquid or solid oxidizers shall be maintained in accordance chapter 9 and remain in accordance with the applicable building code. 6304.1.2 Automatic sprinkler system. The automatic sprinkler system for oxidizer storage shall be maintained in accordance with Chapter 9 and remain in accordance with the applicable building code. 6304.1.3 In addition to section 5004.12, floors of storage areas for liquid and solid oxidizers shall be maintained as liquidtight construction in accordance with the applicable building code. 6304.1.4 Smoke detection. Smoke detection systems shall be maintained in accordance with Chapter 9 and remain in accordance with the applicable building code. 6304.1.5 Storage conditions. The maximum quantity of oxidizers per building in storage buildings shall not exceed those quantities set forth in tables 6304.1.5(1) through 6304.1.5(3). The storage configuration for liquid and solid oxidizers shall be as set forth in table 6303.2. and Tables 6304.1.5(1) through 6304.1.5(3). Class 2 oxidizers shall not be stored in basements unless approved by the applicable building code. Class 3 and 4 oxidizers in amounts exceeding the maximum allowable quantity per control area set forth in 5003.1, shall be stored on the ground floor only unless otherwise approved by the applicable building code.
TABLE 6304.1.7(2) STORAGE OF CLASS 2 OXIDIZER LIQUIDS AND SOLIDSa, b TABLE 6304.1.7(3) STORAGE OF CLASS 3 OXIDIZER LIQUIDS AND SOLIDSa, b TABLE 6304.1.7(4) STORAGE OF CLASS 4 OXIDIZER LIQUIDS AND SOLIDS | (N)TABLE 6304.1.5(1) STORAGE OF CLASS 2 OXIDIZER LIQUIDS AND SOLIDS (Table deleted) (N)TABLE 6304.1.5(2) STORAGE OF CLASS 3 OXIDIZER LIQUIDS AND SOLIDS (Table deleted) (N)TABLE 6304.1.5(3) STORAGE OF CLASS 4 OXIDIZER LIQUIDS AND SOLIDS (Table deleted) |  |  | Keep tables
6304.2 Outdoor storage. Outdoor storage of oxidizing materials in amounts exceeding the maximum allowable quantities per control area set forth in Table 5003.1.1(3) shall be in accordance with Sections 5001, 5003, 5004 and this chapter. Oxidizing gases shall also comply with Chapter 53. | 6304.1.8 Detached storage. Storage of liquid and solid oxidizers shall be in detached buildings where required by the applicable building code. |  |  | 6304.1.8 Detached storage. Storage of liquid and solid oxidizers shall be maintained in detached buildings as set forth by Section 5003.8.2 and in accordance and comply with the applicable building code.
6304.2.3 Storage configuration for liquid and solid oxidizers. Storage configuration for liquid and solid oxidizers shall be in accordance with or Tables 6304.1.7(1) through 6304.1.7(4). | 6304.2.2 Storage configuration for liquid and solid oxidizers. Storage configuration for liquid and solid oxidizers shall be in accordance with the applicable building code. |  |  | 6304.2.2 Storage configuration for liquid and solid oxidizers. Storage configuration for liquid and solid oxidizers shall be maintained in accordance with table 6303.2 and Tables 6304.1.5(1) through 6304.1.5(3) and comply with the applicable building code.
6305.1 Scope. The use of oxidizers in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1) or 5003.1.1(3) shall be in accordance with Sections 5001, 5003, 5005 and this chapter. Oxidizing gases shall also comply with Chapter 53. | (N)6305.1 Scope. The use of oxidizers shall be in accordance with the applicable building code. |  |  | 6305.1 Scope. The use of oxidizers in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1) or 5003.1.1(3) shall be maintained in accordance with Sections 5001, 5003, 5005, this chapter and comply with the applicable building code. Oxidizing gases shall also comply with Chapter 53.
6306.4 Maximum aggregate quantity. The maximum aggregate quantity of liquid oxygen allowed in storage and in use in each dwelling unit shall be 31.6 gallons (120 L). Exceptions: 1.The maximum aggregate quantity of liquid oxygen allowed in Group I-4 occupancies shall be limited by the maximum allowable quantity set forth in Table 5003.1.1(1). 2.Where individual sleeping rooms are separated from the remainder of the dwelling unit by fire barriers constructed in accordance with Section 707 of the International Building Code, and horizontal assemblies constructed in accordance with Section 711 of the International Building Code, or both, having a minimum fire-resistance rating of 1 hour, the maximum aggregate quantity per dwelling unit shall be increased to allow a maximum of 31.6 gallons (120 L) of liquid oxygen per sleeping room. | (N)6306.4 Maximum aggregate quantity. The maximum aggregate quantity of liquid oxygen allowed in storage and in use in each dwelling unit shall be maintained in accordance with the applicable building code. |  |  | The maximum aggregate quantity of liquid oxygen allowed in storage and in use in each dwelling unit shall be 31.6 gallons (120 L). Exceptions: 1.The maximum aggregate quantity of liquid oxygen allowed in Group I-4 occupancies shall be limited by the maximum allowable quantity set forth in Table 5003.1.1(1). 2.Where individual sleeping rooms are separated from the remainder of the dwelling unit by fire-resistant rated assemblies constructed in accordance with the applicable building code, the maximum aggregate quantity per dwelling unit shall be increased to allow a maximum of 31.6 gallons (120 L) of liquid oxygen per sleeping room.

## Ch64 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
6401.2 Permits. Permits shall be required as set forth in Section 107.2. | 6401.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
6403.1 Quantities not exceeding the maximum allowable quantity per control area. The storage and use of pyrophoric materials in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with Sections 5001, 5003, 6401 and 6403. 6403.1.1 Emergency shutoff. Compressed gas systems conveying pyrophoric gases shall be provided with approved manual or automatic emergency shutoff valves that can be activated at each point of use and at each source | (N)6403.1 Storage and use. The storage and use of pyrophoric material shall be maintained in accordance with the applicable building code. (N)6403.1.1 Emergency shutoff. Emergency shutoff valves shall be maintained in accordance with the applicable building code. |  |  | 6403.1 Quantities not exceeding the maximum allowable quantity per control area. The storage and use of pyrophoric materials in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be maintained in accordance with Sections 5001, 5003, 6401, and 6403. 6403.1.1 Emergency shutoff. Compressed gas systems conveying pyrophoric gases shall be maintained with approved manual or automatic emergency shutoff valves that can be activated at each point of use and at each source in accordance with the applicable building code.
6403.1.1.1 Shutoff at source. An automatic emergency shutoff valve shall be installed on supply piping at the cylinder or bulk source. The shutoff valve shall be operated by a remotely located manually activated shutdown control located not less than 15 feet (4572 mm) from the source of supply. Manual or automatic cylinder valves are allowed to be used as the required emergency shutoff valve when the source of supply is limited to unmanifolded cylinder sources. 6403.1.1.2 Shutoff at point of use. A manual or automatic emergency shutoff valve shall be installed on the supply piping at the point of use or at a point where the equipment using the gas is connected to the supply system. | (N)6403.1.1.1 Shutoff at source. (Section deleted) (N)6403.1.1.2 Shutoff at point of use. (Section deleted) |  |  | no change
6403.2 Quantities exceeding the maximum allowable quantity per control area. The storage and use of pyrophoric materials in amounts exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with Chapter 50 and this chapter. | (N)6403.2 Quantities exceeding the maximum allowable quantity per control area. (Section deleted) |  |  | 6403.2 Quantities exceeding the maximum allowable quantity per control area. The storage and use of pyrophoric materials in amounts exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be maintained in accordance with Chapter 50, this chapter. and comply with the applicable building code.
6404.1 Indoor storage. Indoor storage of pyrophoric materials in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1), shall be in accordance with Sections 5001, 5003 and 5004 and this chapter. The storage of silane gas, and gas mixtures with a silane concentration of 1.37 percent or more by volume, shall be in accordance with CGA G-13. | (N)6404.1 Indoor storage. Indoor storage of pyrophoric materials shall be maintained in accordance with the applicable building code. |  |  | 6404.1 Indoor storage. Indoor storage of pyrophoric materials in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1), shall be in accordance with Sections 5001, 5003 and 5004, this chapter and comply with the applicable building code. The storage of silane gas, and gas mixtures with a silane concentration of 1.37 percent or more by volume, shall be maintained in accordance with CGA G-13.
6404.1.1 Liquid-tight floor. In addition to the requirements of Section 5004.12, floors of storage areas containing pyrophoric liquids shall be of liquid-tight construction. 6404.1.2 Pyrophoric solids and liquids. Storage of pyrophoric solids and liquids shall be limited to a maximum area of 100 square feet (9.3 m2) per pile. Storage shall not exceed 5 feet (1524 mm) in height. Individual containers shall not be stacked. Aisles between storage piles shall be a minimum of 10 feet (3048 mm) in width. Individual tanks or containers shall not exceed 500 gallons (1893 L) in capacity. 6404.1.3 Pyrophoric gases. Storage of pyrophoric gases shall be in detached buildings where required by Section 5003.8.2. 6404.1.4 Separation from incompatible materials. In addition to the requirements of Section 5003.9.8, indoor storage of pyrophoric materials shall be isolated from incompatible hazardous materials by 1-hour fire barriers with openings protected in accordance with the International Building Code. Exception: Storage in approved hazardous materials storage cabinets constructed in accordance with Section 5003.8.7. 6404.2 Outdoor storage. Outdoor storage of pyrophoric materials in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(3) shall be in accordance with Sections 5001, 5003 and 5004, and this chapter. The storage of silane gas, and gas mixtures with a silane concentration of 1.37 percent or more by volume, shall be in accordance with CGA G-13. | (N)6404.1.1 Liquid-tight floor. Liquidtight floors of storage areas containing pyrophoric liquids shall be maintained in accordance with the applicable building code.(N)6404.1.2 Pyrophoric solids and liquids. (Section deleted) (N)6404.1.3 Pyrophoric gases. (Section deleted) (N)6404.1.4 Separation from incompatible materials. (Section deleted) (N)6404.2.2 Outdoor storage. (Section deleted) |  |  | 6404.1.1 Liquid-tight floor. In addition to the requirements of Section 5004.12, floors of storage areas containing pyrophoric liquids shall be maintained liquid-tight in accordance with the applicable building code. 6404.1.2 Pyrophoric solids and liquids. Unless otherwise approved by the applicable building code, storage of pyrophoric solids and liquids shall be limited to the following: A maximum area of 100 square feet (9.3 m2) per pile. Storage shall not exceed 5 feet (1524 mm) in height. Individual containers shall not be stacked. Aisles between storage piles shall be a minimum of 10 feet (3048 mm) in width. Individual tanks or containers shall not exceed 500 gallons (1893 L) in capacity. 6404.1.3 Pyrophoric gases. Storage of pyrophoric gases shall be maintained in detached buildings in accordance with Section 5003.8.2 and comply with the applicable building code. 6404.1.4 Separation from incompatible materials. In addition to the requirements of Section 5003.9.8, indoor storage of pyrophoric materials shall be isolated from incompatible hazardous materials by fire-resistance rated construction with openings protected in accordance with the applicable building code. Exception: Storage in approved hazardous materials storage cabinets constructed in accordance with Section 5003.8.7. 6404.2 Outdoor storage. Outdoor storage of pyrophoric materials in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(3) shall be maintained in accordance with Sections 5001, 5003 and 5004, this chapter and comply with the applicable building code.. The storage of silane gas, and gas mixtures with a silane concentration of 1.37 percent or more by volume, shall be maintained in accordance with CGA G-13.

## Ch65 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
6501.2 Permits. Permits shall be required as set forth in Section 107.2. | 6501.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
6504.1 Raw material. Raw cellulose nitrate (pyroxylin) plastic material in a Group F building shall be stored and handled in accordance with Sections 6504.1.1 through 6504.1.7. | 6504.1 Raw material. Raw cellulose nitrate (pyroxylin) plastic material in a Group F building shall be stored and handled in accordance with Sections 6504.1.2 and 6504.1.4 through 6504.1.7. |  |  | 6504.1 Raw material. Raw cellulose nitrate (pyroxylin) plastic material in a Group F building shall be stored and handled in accordance with Sections 6504.1.1 through 6504.1.7.
6504.1.1 Storage of incoming material. Where raw material in excess of 25 pounds (11 kg) is received in a building or fire area, an approved vented cabinet or approved vented vault equipped with an approved automatic sprinkler system shall be provided for the storage of material. | (N)6504.1.1 Storage of incoming material. (Section deleted) |  |  | 6504.1.1 Storage of incoming material. Unless otherwise approved by the applicable building code, where raw material in excess of 25 pounds (11 kg) is received in a building or fire area, it shall be stored in an approved vented cabinet or approved vented vault equipped with an approved automatic sprinkler system in accordance with the applicable building code.
6504.1.3 Storage of additional material. Raw material in excess of that allowed by Section 6504.1.2 shall be kept in vented vaults not exceeding 1,500-cubic-foot capacity (43 m3) of total vault space, and with approved construction, venting and sprinkler protection. | (N)6504.1.3 Storage of additional material. (Section deleted) |  |  | 6504.1.3 Storage of additional material. Raw material in excess of that allowed by Section 6504.1.2 shall remain stored in vented vaults or other arrangement approved in accordance with the applicable building code.
6504.2 Fire protection. The manufacture or storage of articles of cellulose nitrate (pyroxylin) plastic in quantities exceeding 100 pounds (45 kg) shall be located in a building or portion thereof equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1. | (N)6504.2 Fire protection. Fire protection for the manufacture or storage of articles of cellulose nitrate (pyroxylin) plastic in quantities exceeding 100 pounds (45 kg) shall be in accordance with the applicable building code. |  |  | 6504.2 Fire protection. The manufacture or storage of articles of cellulose nitrate (pyroxylin) plastic in quantities exceeding 100 pounds (45 kg) shall remain located in a building or portion thereof equipped throughout with an approved automatic sprinkler system in accordance with NFPA 13 and the applicable building code.

## Ch66 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
6601.2 Permits. Permits shall be required as set forth in Section 107.2. | 6601.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | No change
6603.1 Quantities not exceeding the maximum allowable quantity per control area. Quantities of unstable (reactive) materials not exceeding the maximum allowable quantity per control area shall be in accordance with Sections 6603.1.1 through 6603.1.2.5. 6603.1.1 General. The storage and use of unstable (reactive) materials in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with Sections 5001, 5003, 6601 and 6603. | (N)6603.1 Storage and use. Quantities of unstable (reactive) materials not exceeding the maximum allowable quantity per control area shall be maintained in accordance with the applicable building code. (N)6603.1.1 General. The storage and use of unstable (reactive) materials shall be in accordance with the applicable building code. |  |  | 6603.1 Quantities not exceeding the maximum allowable quantity per control area. Quantities of unstable (reactive) materials not exceeding the maximum allowable quantity per control area shall be in accordance with Sections 6603.1.1 through 6603.1.2.5. 6603.1.1 General. The storage and use of unstable (reactive) materials in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with Sections 5001, 5003, 6601 and 6603.
6603.1.2 Limitations for indoor storage and use by occupancy. The indoor storage of unstable (reactive) materials shall be in accordance with Sections 6603.1.2.1 through 6603.1.2.5. | (N)6603.1.2 Limitations for indoor storage and use by occupancy. (Section deleted) |  |  | 6603.1.2 Limitations for indoor storage and use by occupancy. The indoor storage of unstable (reactive) materials shall be maintained in accordance with Sections 6603.1.2.1 through 6603.1.2.5 and comply with the applicable building code.
6603.1.2.1 Group A, E, I or U occupancies. In Group A, E, I or U occupancies, any amount of Class 3 and 4 unstable (reactive) materials shall be stored in accordance with the following: 1.Class 3 and 4 unstable (reactive) materials shall be stored in hazardous material storage cabinets complying with Section 5003.8.7. 2.The hazardous material storage cabinets shall not contain other storage. | 6603.1.2.1 Group A, E, I or U occupancies. In Group A, E, I or U occupancies, any amount of Classes 3 and 4 unstable (reactive) materials shall be stored in accordance with the applicable building code. |  |  | 6603.1.2.1 Group A, E, I or U occupancies. Unless otherwise approved by the applicable building code, in Group A, E, I or U occupancies, any amount of Class 3 and 4 unstable (reactive) materials shall be stored in accordance with the following: 1.Class 3 and 4 unstable (reactive) materials shall be stored in hazardous material storage cabinets complying with Section 5003.8.7. 2.The hazardous material storage cabinets shall not contain other storage.
6604.1 Indoor storage. Indoor storage of unstable (reactive) materials in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1) shall be in accordance with Sections 5001, 5003, 5004 and this chapter. In addition, Class 3 and 4 unstable (reactive) detonable materials shall be stored in accordance with the International Building Code requirements for explosives. | (N)6604.1 Indoor storage. Indoor storage of unstable (reactive) materials shall be maintained in accordance with the applicable building code. |  |  | 6604.1 Indoor storage. Indoor storage of unstable (reactive) materials in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1) shall be maintained in accordance with Sections 5001, 5003, 5004, this chapter and comply with the applicable building code. In addition, Class 3 and 4 unstable (reactive) detonable materials shall be stored in accordance with the applicable building code requirements for explosives.
6604.1.1 Detached storage. Storage of unstable (reactive) materials shall be in detached buildings when required in Section 5003.8.2. | (N)6604.1.1 Detached storage. (Section deleted) |  |  | 6604.1.1 Detached storage. Storage of unstable (reactive) materials shall be in detached buildings when required in Section 5003.8.2.
6604.1.2 Explosion control. Indoor storage rooms, areas and buildings containing Class 3 or 4 unstable (reactive) materials shall be provided with explosion control in accordance with Section 911. | (N)6604.1.2 Explosion control. Explosion control for indoor storage shall be maintained in accordance with the applicable building code. |  |  | 6604.1.2 Explosion control. Indoor storage rooms, areas and buildings containing Class 3 or 4 unstable (reactive) materials shall be maintained with explosion control in accordance with Section 911 and remain in accordance with the applicable building code.
6604.1.3 Liquid-tight floor. In addition to Section 5004.12, floors of storage areas for liquids and solids shall be of liquid-tight construction. | (N)6604.1.3 Liquid-tight floor. Liquid-tight floors of storage areas shall be maintained in accordance with the applicable building code. (N)6604.1.5 Location in building. Unstable (reactive) materials shall not be stored in basements unless approved. |  |  | No change

## Ch67 (hidden)
2012 VSFPC | 2015 VSFPC Amendment | 2018 IFC | Notes | VFSB CSC Recommendation | VFSB CSC Vote
6701.2 Permits. Permits shall be required as set forth in Section 105.6. | 6701.2 Permits. Permits shall be required as set forth in Section 107.2. |  |  | no change
6703.1 Quantities not exceeding the maximum allowable quantity per control area. The storage and use of water-reactive solids and liquids in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with Sections 5001, 5003, 6701 and 6703. | (N)6703.1 Storage and use. The storage and use of water reactive solids and liquids shall be maintained in accordance with the applicable building code. |  |  | 6703.1 Quantities not exceeding the maximum allowable quantity per control area. The storage and use of water-reactive solids and liquids in amounts not exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be maintained in accordance with Sections 5001, 5003, 6701 and 6703.
6703.2 Quantities exceeding the maximum allowable quantity per control area. The storage and use of water-reactive solids and liquids in amounts exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be in accordance with Chapter 50 and this chapter. | (N)6703.2 Quantities exceeding the maximum allowable quantity per control area. (Section deleted) |  |  | 6703.2 Quantities exceeding the maximum allowable quantity per control area. The storage and use of water-reactive solids and liquids in amounts exceeding the maximum allowable quantity per control area indicated in Section 5003.1 shall be maintained in accordance with Chapter 50, this chapter and comply with the applicable building code.
6704.1 Indoor storage. Indoor storage of water-reactive solids and liquids in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1), shall be in accordance with Sections 5001, 5003, 5004 and this chapter. | (N)6704.1 Indoor storage. Indoor storage of water-reactive solids and liquids shall be maintained in accordance with the applicable building code. |  |  | 6704.1 Indoor storage. Indoor storage of water-reactive solids and liquids in amounts exceeding the maximum allowable quantity per control area indicated in Table 5003.1.1(1), shall be maintained in accordance with Sections 5001, 5003, 5004, this chapter and comply with the applicable building code.
6704.1.1 Detached storage. Storage of water-reactive solids and liquids shall be in detached buildings when required by Section 5003.8.2. | (N)6704.1.1 Detached storage. (Section deleted) |  |  | 6704.1.1 Detached storage. The storage of water-reactive solids and liquids shall be maintained in detached buildings as set forth by Section 5003.8.2 and remain in accordance with the applicable building code.
6704.1.2 Liquid-tight floor. In addition to the provisions of Section 5004.12, floors in storage areas for water-reactive solids and liquids shall be of liquid-tight construction. | (N)6704.1.2 Liquid-tight floor. Liquid-tight floors in storage areas for water reactive solids and liquids shall be maintained in accordance with the applicable building code. |  |  | 6704.1.2 Liquid-tight floor. In addition to the provisions of Section 5004.12, floors in storage areas for water-reactive solids and liquids shall be maintained liquid-tight in accordance with the applicable building code.
6704.1.3 Waterproof room. Rooms or areas used for the storage of water-reactive solids and liquids shall be constructed in a manner which resists the penetration of water through the use of waterproof materials. Piping carrying water for other than approved automatic sprinkler systems shall not be within such rooms or areas. | (N)6704.1.3 Waterproof room. (Section deleted) |  |  | 6704.1.3 Waterproof room. Rooms or areas used for the storage of water-reactive solids and liquids shall be maintained in a manner which resists the penetration of water in accordance with the applicable building code.
6704.1.5 Storage configuration. Water-reactive solids and liquids stored in quantities greater than 500 cubic feet (14 m3) shall be separated into piles, each not larger than 500 cubic feet (14 m3). Aisle widths between piles shall not be less than the height of the pile or 4 feet (1219 mm), whichever is greater. Exception: Water-reactive solids and liquids stored in tanks. Class 2 water-reactive solids and liquids shall not be stored in basements unless such materials are stored in closed water-tight containers or tanks. Class 3 water-reactive solids and liquids shall not be stored in basements. Class 2 or 3 water-reactive solids and liquids shall not be stored with flammable liquids. | (N)6704.1.5 Storage configuration. Aisle widths between piles shall be maintained in accordance with the applicable building code. |  |  | 6704.1.5 Storage configuration. Water-reactive solids and liquids stored in quantities greater than 500 cubic feet (14 m3) shall be maintained separated into piles, each not larger than 500 cubic feet (14 m3) unless otherwise approved by the applicabale building code. Aisle widths between piles shall not be less than the height of the pile or 4 feet (1219 mm), whichever is greater. Exception: Water-reactive solids and liquids stored in tanks. Class 2 water-reactive solids and liquids shall not be stored in basements unless such materials are stored in closed water-tight containers or tanks. Class 3 water-reactive solids and liquids shall not be stored in basements. Class 2 or 3 water-reactive solids and liquids shall not be stored with flammable liquids.
6704.1.6 Explosion control. Indoor storage rooms, areas and buildings containing Class 2 or 3 water-reactive solids and liquids shall be provided with explosion control in accordance with Section 911. | (N)6704.1.6 Explosion control. Explosion control for indoor storage rooms shall be maintained in accordance with the applicable building code. |  |  | 6704.1.6 Explosion control. Indoor storage rooms, areas and buildings containing Class 2 or 3 water-reactive solids and liquids shall be maintained with explosion control in accordance with Section 911 and comply with the applicable building code.
6704.2.5 Containment. Secondary containment shall be provided in accordance with the provisions of Section 5004.2.2. | (N)6704.2.5 Containment. Secondary containment shall be provided in accordance with the applicable building code. |  |  | 6704.2.5 Containment. Secondary containment shall be maintained in accordance with the provisions of Section 5004.2.2 and remain in accordance with the applicable building code.